## Materials + Factor
Project No: |  | M124010 | Ref: | [7 empty] | Sheet No: |  |  | 4 |  | of |  | 120 |  | 4
Project Name: |  | Greek Street Overbridge Replacement | [8 empty] | Date: |  |  | 2025-07-14 10:27
Calculations for: |  | Full Calculations | [8 empty] | By: |  |  | KH1
| Concrete Density | [11 empty] | = | 25
| Bearing capacity | [11 empty] | = | 150
| Ground Properties |  |  | gs
| Strata Name |  | Density |  |  | cu |  |  | j' |  |  | c' |  | thickness
|  |  |  | kN/m3 |  | kPa |  |  | Deg |  |  | kPa |  |  | m
Embedded Strata
| Alluvium |  | 18 |  |  |  |  | 32 |  |  | 0 |  |  | 3
Founding Strata
| RTD |  | 18 |  |  |  |  | 32 |  |  | 0 |  |  | 0
| Ground Water Level |  |  |  | = |  | 3 |  |  | m | BGL |  |  | SLS
| Worst Water Level |  |  |  | = |  | 3 |  |  | m | BGL |  |  | DA1.1 / DA1.2
| Water Unit Weight |  |  | (gw) | = |  | 9.81 |  |  |  | kN/m3
| Friction coefficient | [11 empty] | = | 0.50935
| Benefical vertical Load factor | [11 empty] | = | 0 |  |  | (used)
| Cobcrete load factor | [11 empty] | = | 1.35 |  |  | (used)
FM-AD-002-07 | [18 empty] | Tony Gee and Partners

## Loading Summary (ss) (hidden)
| Input Values |  |  | All foundations are square so B = L | [7 empty] | 7.5
[8 empty] | Foundation Depth (m) = |  |  |  |  | 0.75 | m | Foundation Depth (m) = |  |  |  |  | 1 | m | Foundation Depth (m) = |  |  |  |  | 2 | m
Name | Loadcase | Vertical Fz (kN) | Beneficial Vertical (kN) | ¦¦ to Span, Fy (kN) | ⊥ to Span, Fx (kN) | Moment about ¦¦, My (kNm) | Moment about ⊥, Mx (kNm) | Base Size (B)1 | e'B1 | e'L1 | Sliding1 | Over-turning1 | Mid Third1 | Bearing1 | Base Size (B)2 | e'B2 | e'L2 | Sliding2 | Over-turning2 | Mid Third2 | Bearing2 | Base Size (B)3 | e'B3 | e'L3 | Sliding3 | Over-turning3 | Mid Third3 | Bearing3
400kV High Level - Post Insulator Structure x 7150mm high | MAX | 28.23 |  | 7.8 | 14.57 | 144.67 | 55.86 | 3.7 |  | Worst Load Case = | 11.14% | 32.77% | 91.4% | 26.23% | 3.4 |  | Worst Load Case = | 9.898% | 32.41% | 88.34% | 34.25% | 2.7 |  | Worst Load Case = | 7.848% | 35.32% | 88.2% | 67.82%
| 1 | 17.37 | 0 | 0 | 13.88 | 137.78 | 0 | 3.7 | 0.53676 | 0 | 10.62% | 31.21% | 87.04% | 24.96% | 3.4 | 0.47675 | 0 | 9.429% | 30.87% | 84.13% | 32.66% | 2.7 | 0.378 | 0 | 7.476% | 33.64% | 84% | 64.71%
| 2 | 17.37 | 0 | 4.24 | 5.6 | 66.39 | 23.66 | 3.7 | 0.25864 | 0.092174 | 5.372% | 14.87% | 41.94% | 21.68% | 3.4 | 0.22972 | 0.081869 | 4.772% | 14.65% | 40.54% | 28.55% | 2.7 | 0.18214 | 0.064911 | 3.783% | 15.77% | 40.48% | 56.57%
| 3 | 20.16 | 0 | 0 | 8.8 | 76.5 | 0 | 3.7 | 0.29803 | 0 | 6.731% | 17.5% | 48.33% | 21.29% | 3.4 | 0.26471 | 0 | 5.978% | 17.36% | 46.71% | 28.03% | 2.7 | 0.20988 | 0 | 4.74% | 19.12% | 46.64% | 55.47%
| 4 | 17.37 | 0 | 4.44 | 0 | 0 | 24.85 | 3.7 | 0 | 0.09681 | 3.396% | 5.934% | 15.7% | 18.7% | 3.4 | 0 | 0.085986 | 3.016% | 5.962% | 15.17% | 24.75% | 2.7 | 0 | 0.068176 | 2.391% | 6.855% | 15.15% | 49.07%
| 5 | 17.37 | 0 | 0.72 | 13.72 | 135.84 | 8.58 | 3.7 | 0.5292 | 0.033426 | 10.51% | 30.77% | 85.82% | 25.28% | 3.4 | 0.47003 | 0.029689 | 9.333% | 30.44% | 82.95% | 33.06% | 2.7 | 0.37267 | 0.023539 | 7.4% | 33.18% | 82.82% | 65.5%
| 6 | 20.16 | 0 | 5.49 | 5.5 | 65.16 | 38.43 | 3.7 | 0.25385 | 0.14972 | 5.944% | 14.59% | 41.16% | 22.52% | 3.4 | 0.22547 | 0.13298 | 5.279% | 14.38% | 39.79% | 29.6% | 2.7 | 0.17877 | 0.10543 | 4.186% | 15.48% | 39.73% | 58.57%
| 7 | 20.16 | 0 | 0 | 8.73 | 75.62 | 0 | 3.7 | 0.2946 | 0 | 6.677% | 17.3% | 47.77% | 21.24% | 3.4 | 0.26166 | 0 | 5.931% | 17.17% | 46.18% | 27.97% | 2.7 | 0.20746 | 0 | 4.702% | 18.92% | 46.1% | 55.35%
| 8 | 20.16 | 0 | 5.01 | 0 | 0 | 31.54 | 3.7 | 0 | 0.12287 | 3.832% | 7.433% | 19.93% | 19.13% | 3.4 | 0 | 0.10913 | 3.403% | 7.439% | 19.26% | 25.29% | 2.7 | 0 | 0.086529 | 2.699% | 8.446% | 19.23% | 50.05%
| 9 | 17.37 | 0 | 1.45 | 13.55 | 133.89 | 17.16 | 3.7 | 0.52161 | 0.066852 | 10.42% | 30.34% | 84.58% | 25.6% | 3.4 | 0.46329 | 0.059377 | 9.258% | 30.01% | 81.76% | 33.47% | 2.7 | 0.36733 | 0.047078 | 7.34% | 32.72% | 81.63% | 66.32%
| 10 | 17.37 | 0 | 6.74 | 5.41 | 64.03 | 53.2 | 3.7 | 0.24945 | 0.20726 | 6.61% | 14.34% | 40.45% | 23.07% | 3.4 | 0.22156 | 0.18408 | 5.871% | 14.13% | 39.1% | 30.31% | 2.7 | 0.17567 | 0.14595 | 4.655% | 15.21% | 39.04% | 60.05%
| 11 | 20.16 | 0 | 0 | 8.66 | 74.74 | 0 | 3.7 | 0.29117 | 0 | 6.624% | 17.11% | 47.22% | 21.19% | 3.4 | 0.25862 | 0 | 5.883% | 16.98% | 45.64% | 27.91% | 2.7 | 0.20505 | 0 | 4.664% | 18.71% | 45.57% | 55.23%
| 12 | 20.16 | 0 | 5.57 | 0 | 0 | 38.22 | 3.7 | 0 | 0.1489 | 4.26% | 8.928% | 24.15% | 19.42% | 3.4 | 0 | 0.13225 | 3.784% | 8.913% | 23.34% | 25.66% | 2.7 | 0 | 0.10486 | 3% | 10.03% | 23.3% | 50.79%
| 13 | 18.24 | 0 | 0 | 14.57 | 144.67 | 0 | 3.7 | 0.5636 | 0 | 11.14% | 32.77% | 91.4% | 25.55% | 3.4 | 0.50059 | 0 | 9.898% | 32.41% | 88.34% | 33.38% | 2.7 | 0.3969 | 0 | 7.848% | 35.32% | 88.2% | 66.1%
| 14 | 18.24 | 0 | 4.45 | 5.88 | 69.6 | 24.84 | 3.7 | 0.27115 | 0.096771 | 5.64% | 15.59% | 43.97% | 21.96% | 3.4 | 0.24083 | 0.085952 | 5.009% | 15.36% | 42.5% | 28.9% | 2.7 | 0.19095 | 0.068148 | 3.972% | 16.53% | 42.43% | 57.25%
| 15 | 28.23 | 0 | 0 | 12.33 | 107.1 | 0 | 3.7 | 0.41724 | 0 | 9.431% | 24.5% | 67.66% | 23.56% | 3.4 | 0.37059 | 0 | 8.376% | 24.31% | 65.4% | 30.85% | 2.7 | 0.29383 | 0 | 6.641% | 26.78% | 65.29% | 60.82%
| 16 | 28.23 | 0 | 6.22 | 0 | 0 | 34.79 | 3.7 | 0 | 0.13553 | 4.757% | 8.309% | 21.98% | 19.69% | 3.4 | 0 | 0.12038 | 4.225% | 8.347% | 21.24% | 25.97% | 2.7 | 0 | 0.095446 | 3.35% | 9.598% | 21.21% | 51.2%
| 17 | 18.24 | 0 | 0.76 | 14.4 | 142.63 | 9.01 | 3.7 | 0.55566 | 0.035101 | 11.03% | 32.31% | 90.11% | 25.88% | 3.4 | 0.49353 | 0.031176 | 9.796% | 31.96% | 87.09% | 33.81% | 2.7 | 0.3913 | 0.024719 | 7.767% | 34.84% | 86.96% | 66.94%
| 18 | 18.24 | 0 | 5.76 | 5.78 | 68.41 | 40.25 | 3.7 | 0.26651 | 0.15681 | 6.241% | 15.32% | 43.22% | 22.67% | 3.4 | 0.23671 | 0.13927 | 5.543% | 15.1% | 41.77% | 29.8% | 2.7 | 0.18768 | 0.11043 | 4.395% | 16.25% | 41.71% | 59.03%
| 19 | 28.23 | 0 | 0 | 12.22 | 105.87 | 0 | 3.7 | 0.41245 | 0 | 9.347% | 24.22% | 66.88% | 23.49% | 3.4 | 0.36633 | 0 | 8.302% | 24.04% | 64.65% | 30.76% | 2.7 | 0.29045 | 0 | 6.582% | 26.48% | 64.55% | 60.63%
| 20 | 28.23 | 0 | 7.01 | 0 | 0 | 44.15 | 3.7 | 0 | 0.172 | 5.362% | 10.4% | 27.89% | 20.12% | 3.4 | 0 | 0.15277 | 4.762% | 10.41% | 26.96% | 26.51% | 2.7 | 0 | 0.12112 | 3.776% | 11.82% | 26.92% | 52.27%
| 21 | 18.24 | 0 | 1.52 | 14.23 | 140.59 | 18.01 | 3.7 | 0.54771 | 0.070163 | 10.95% | 31.85% | 88.82% | 26.23% | 3.4 | 0.48647 | 0.062318 | 9.722% | 31.51% | 85.85% | 34.25% | 2.7 | 0.38571 | 0.04941 | 7.708% | 34.35% | 85.71% | 67.82%
| 22 | 18.24 | 0 | 7.07 | 5.68 | 67.23 | 55.86 | 3.7 | 0.26191 | 0.21762 | 6.936% | 15.05% | 42.47% | 23.45% | 3.4 | 0.23263 | 0.19329 | 6.161% | 14.84% | 41.05% | 30.79% | 2.7 | 0.18444 | 0.15325 | 4.885% | 15.97% | 40.99% | 60.97%
| 23 | 28.23 | 0 | 0 | 12.12 | 104.64 | 0 | 3.7 | 0.40766 | 0 | 9.27% | 23.95% | 66.11% | 23.41% | 3.4 | 0.36208 | 0 | 8.234% | 23.77% | 63.9% | 30.66% | 2.7 | 0.28708 | 0 | 6.528% | 26.19% | 63.8% | 60.43%
| 24 | 28.23 | 0 | 7.8 | 0 | 0 | 53.51 | 3.7 | 0 | 0.20846 | 5.966% | 12.5% | 33.8% | 20.57% | 3.4 | 0 | 0.18516 | 5.299% | 12.48% | 32.67% | 27.08% | 2.7 | 0 | 0.1468 | 4.201% | 14.04% | 32.62% | 53.39%
400kV Low Level - Post Insulator Structure x 2750mm high | MAX | 7.87 |  | 5.36 | 2.87 | 13.31 | 30.65 | 1.7 |  | Worst Load Case = | 19.42% | 75.27% | 86.69% | 54.05% | 1.6 |  | Worst Load Case = | 16.44% | 70.33% | 77.99% | 59.46% | 1.4 |  | Worst Load Case = | 10.74% | 60.31% | 58.21% | 84.57%
| 1 | 4.99 | 0 | 3.51 | 1.86 | 6.99 | 23.99 | 1.7 | 0.129 | 0.44272 | 14.39% | 57.8% | 45.53% | 44.35% | 1.6 | 0.10922 | 0.37484 | 12.19% | 53.71% | 40.96% | 51.86% | 1.4 | 0.071327 | 0.2448 | 7.958% | 45.2% | 30.57% | 79.96%
| 2 | 4.99 | 0 | 5.1 | 0 | 0 | 29.19 | 1.7 | 0 | 0.53869 | 18.48% | 71.68% | 53.87% | 49.22% | 1.6 | 0 | 0.45609 | 15.64% | 66.97% | 45.61% | 55.36% | 1.4 | 0 | 0.29786 | 10.22% | 57.42% | 29.79% | 81.28%
| 3 | 5.62 | 0 | 1.16 | 2.05 | 9.51 | 7.96 | 1.7 | 0.1755 | 0.1469 | 8.534% | 23.99% | 61.94% | 27.68% | 1.6 | 0.14859 | 0.12437 | 7.226% | 22.58% | 55.72% | 34.85% | 1.4 | 0.097041 | 0.081224 | 4.719% | 19.84% | 41.59% | 61.61%
| 4 | 5.62 | 0 | 2.57 | 0 | 0 | 11.5 | 1.7 | 0 | 0.21223 | 9.311% | 29.15% | 21.22% | 24.22% | 1.6 | 0 | 0.17969 | 7.884% | 27.48% | 17.97% | 30.91% | 1.4 | 0 | 0.11735 | 5.149% | 24.26% | 11.73% | 56.36%
| 5 | 5.24 | 0 | 3.68 | 1.95 | 7.34 | 25.19 | 1.7 | 0.13546 | 0.46487 | 15.09% | 60.68% | 47.81% | 47.48% | 1.6 | 0.11469 | 0.39359 | 12.78% | 56.39% | 43.01% | 54.84% | 1.4 | 0.074898 | 0.25704 | 8.343% | 47.45% | 32.1% | 82.79%
| 6 | 5.24 | 0 | 5.36 | 0 | 0 | 30.65 | 1.7 | 0 | 0.56563 | 19.42% | 75.27% | 56.56% | 54.05% | 1.6 | 0 | 0.47891 | 16.44% | 70.33% | 47.89% | 59.46% | 1.4 | 0 | 0.31276 | 10.74% | 60.31% | 31.28% | 84.57%
| 7 | 7.87 | 0 | 1.63 | 2.87 | 13.31 | 11.14 | 1.7 | 0.24563 | 0.20558 | 11.96% | 33.57% | 86.69% | 34.67% | 1.6 | 0.20797 | 0.17406 | 10.12% | 31.6% | 77.99% | 42.4% | 1.4 | 0.13582 | 0.11367 | 6.612% | 27.77% | 58.21% | 70.62%
| 8 | 7.87 | 0 | 3.6 | 0 | 0 | 16.1 | 1.7 | 0 | 0.29712 | 13.04% | 40.82% | 29.71% | 28.73% | 1.6 | 0 | 0.25156 | 11.04% | 38.48% | 25.16% | 35.81% | 1.4 | 0 | 0.16429 | 7.212% | 33.97% | 16.43% | 62.3%
400kV Surge Arrester Structure x 2400mm high | MAX | 9.11 |  | 5.91 | 3.24 | 12.29 | 35.68 | 2.3 |  | Worst Load Case = | 11.7% | 35.17% | 93.84% | 25.67% | 2.1 |  | Worst Load Case = | 10.52% | 35.93% | 92.47% | 33.85% | 1.7 |  | Worst Load Case = | 8.03% | 38.67% | 87.15% | 65.39%
| 1 | 5.77 | 0 | 3.71 | 2.11 | 7.88 | 27.4 | 2.3 | 0.079445 | 0.27624 | 8.448% | 26.46% | 72.06% | 24.89% | 2.1 | 0.071474 | 0.24853 | 7.6% | 26.87% | 71.01% | 32.86% | 1.7 | 0.054533 | 0.18962 | 5.799% | 28.35% | 66.92% | 63.72%
| 2 | 5.77 | 0 | 0.63 | 0 | 0 | 33.98 | 2.3 | 0 | 0.34258 | 1.247% | 30.2% | 89.37% | 25.07% | 2.1 | 0 | 0.30821 | 1.122% | 29.9% | 88.06% | 33.08% | 1.7 | 0 | 0.23516 | 0.856% | 28.69% | 83% | 64.05%
| 3 | 6.51 | 0 | 0.78 | 2.32 | 8.78 | 5.73 | 2.3 | 0.088519 | 0.057769 | 4.845% | 9.223% | 23.09% | 20.19% | 2.1 | 0.079637 | 0.051973 | 4.359% | 9.589% | 22.75% | 26.73% | 1.7 | 0.060761 | 0.039654 | 3.326% | 10.93% | 21.45% | 52.53%
| 4 | 6.51 | 0 | 2.66 | 0 | 0 | 11.35 | 2.3 | 0 | 0.11443 | 5.265% | 11.7% | 29.85% | 19.65% | 2.1 | 0 | 0.10295 | 4.737% | 12.1% | 29.41% | 26.04% | 1.7 | 0 | 0.078547 | 3.614% | 13.57% | 27.72% | 51.24%
| 5 | 6.06 | 0 | 3.89 | 2.21 | 8.28 | 28.77 | 2.3 | 0.083478 | 0.29006 | 8.856% | 27.78% | 75.67% | 25.43% | 2.1 | 0.075102 | 0.26095 | 7.967% | 28.21% | 74.56% | 33.56% | 1.7 | 0.057301 | 0.1991 | 6.079% | 29.76% | 70.27% | 64.97%
| 6 | 6.06 | 0 | 5.91 | 0 | 0 | 35.68 | 2.3 | 0 | 0.35972 | 11.7% | 35.17% | 93.84% | 25.67% | 2.1 | 0 | 0.32363 | 10.52% | 35.93% | 92.47% | 33.85% | 1.7 | 0 | 0.24692 | 8.03% | 38.67% | 87.15% | 65.39%
| 7 | 9.11 | 0 | 1.09 | 3.24 | 12.29 | 8.02 | 2.3 | 0.12391 | 0.080857 | 6.766% | 12.9% | 32.32% | 21.73% | 2.1 | 0.11147 | 0.072744 | 6.087% | 13.42% | 31.85% | 28.7% | 1.7 | 0.085052 | 0.055502 | 4.645% | 15.28% | 30.02% | 55.99%
| 8 | 9.11 | 0 | 3.72 | 0 | 0 | 15.9 | 2.3 | 0 | 0.1603 | 7.363% | 16.39% | 41.82% | 20.94% | 2.1 | 0 | 0.14422 | 6.624% | 16.95% | 41.21% | 27.68% | 1.7 | 0 | 0.11003 | 5.054% | 19% | 38.84% | 54.11%
400kV Earth Switch Structure x 2900mm high | MAX | 26.788 |  | 8.97 | 7.34 | 36.786 | 13.127 | 2.4 |  | Worst Load Case = | 16.31% | 32.19% | 85.15% | 26.24% | 2.2 |  | Worst Load Case = | 14.55% | 32.58% | 82.91% | 34.24% | 1.8 |  | Worst Load Case = | 10.87% | 34.26% | 75.69% | 64.71%
| N4 - L1 | 3.937 | 0 | 1.26 | 0 | 0 | 5.292 | 2.4 | 0 | 0.049 | 2.291% | 4.812% | 12.25% | 18.07% | 2.2 | 0 | 0.043736 | 2.044% | 4.923% | 11.93% | 24% | 1.8 | 0 | 0.032667 | 1.527% | 5.358% | 10.89% | 47.54%
| N4 - L2 | 7.519 | 0 | 1.626 | 2.801 | 9.919 | 0.034 | 2.4 | 0.091843 | 0.00031481 | 5.888% | 9.274% | 22.96% | 19.22% | 2.2 | 0.081975 | 0.00028099 | 5.255% | 9.557% | 22.36% | 25.44% | 1.8 | 0.061228 | 0.00020988 | 3.925% | 10.65% | 20.41% | 49.96%
| N4 - L3 | 5.668 | 0 | 5.158 | 0 | 0 | 8.65 | 2.4 | 0 | 0.080093 | 9.377% | 9.659% | 20.02% | 18.78% | 2.2 | 0 | 0.071488 | 8.369% | 10.37% | 19.5% | 24.9% | 1.8 | 0 | 0.053395 | 6.251% | 13.01% | 17.8% | 49.08%
| N4 - L4 | 9.249 | 0 | 2.272 | 2.801 | 9.919 | 3.391 | 2.4 | 0.091843 | 0.031398 | 6.556% | 9.274% | 22.96% | 19.95% | 2.2 | 0.081975 | 0.028025 | 5.852% | 9.557% | 22.36% | 26.36% | 1.8 | 0.061228 | 0.020932 | 4.371% | 10.65% | 20.41% | 51.53%
| N4 - L5 | 7.695 | 0 | 4.874 | 0 | 0 | 8.856 | 2.4 | 0 | 0.082 | 8.86% | 9.654% | 20.5% | 19.07% | 2.2 | 0 | 0.07319 | 7.908% | 10.32% | 19.96% | 25.24% | 1.8 | 0 | 0.054667 | 5.907% | 12.76% | 18.22% | 49.6%
| N4 - L6 | 11.277 | 0 | 1.988 | 2.801 | 9.919 | 3.597 | 2.4 | 0.091843 | 0.033306 | 6.244% | 9.274% | 22.96% | 20.25% | 2.2 | 0.081975 | 0.029727 | 5.573% | 9.557% | 22.36% | 26.71% | 1.8 | 0.061228 | 0.022204 | 4.163% | 10.65% | 20.41% | 52.06%
| N4 - L7 | 4.519 | 0 | 1.3 | 1.203 | 9.32 | 5.062 | 2.4 | 0.086296 | 0.04687 | 3.22% | 7.888% | 21.57% | 19.51% | 2.2 | 0.077025 | 0.041835 | 2.874% | 7.906% | 21.01% | 25.85% | 1.8 | 0.057531 | 0.031247 | 2.147% | 8.043% | 19.18% | 50.83%
| N4 - L8 | 7.907 | 0 | 1.501 | 4.384 | 22.03 | 0.006 | 2.4 | 0.20398 | 5.5556e-05 | 8.424% | 19.54% | 51% | 21.43% | 2.2 | 0.18207 | 4.9587e-05 | 7.519% | 19.85% | 49.65% | 28.27% | 1.8 | 0.13599 | 3.7037e-05 | 5.616% | 21.12% | 45.33% | 54.93%
| N4 - L9 | 6.093 | 0 | 4.846 | 0.253 | 0.766 | 8.117 | 2.4 | 0.0070926 | 0.075157 | 8.821% | 9.068% | 18.79% | 18.87% | 2.2 | 0.0063306 | 0.067083 | 7.874% | 9.739% | 18.3% | 25% | 1.8 | 0.0047284 | 0.050105 | 5.881% | 12.21% | 16.7% | 49.24%
| N4 - L10 | 9.482 | 0 | 2.045 | 3.434 | 13.476 | 3.061 | 2.4 | 0.12478 | 0.028343 | 7.266% | 12.39% | 31.19% | 20.54% | 2.2 | 0.11137 | 0.025298 | 6.485% | 12.7% | 30.37% | 27.11% | 1.8 | 0.083185 | 0.018895 | 4.844% | 13.95% | 27.73% | 52.84%
| N4 - L11 | 7.938 | 0 | 4.587 | 0.126 | 0.377 | 8.304 | 2.4 | 0.0034907 | 0.076889 | 8.342% | 9.062% | 19.22% | 19.07% | 2.2 | 0.0031157 | 0.068628 | 7.445% | 9.685% | 18.72% | 25.23% | 1.8 | 0.0023272 | 0.051259 | 5.561% | 11.99% | 17.09% | 49.58%
| N4 - L12 | 11.326 | 0 | 1.787 | 3.055 | 12.333 | 3.248 | 2.4 | 0.11419 | 0.030074 | 6.434% | 11.28% | 28.55% | 20.62% | 2.2 | 0.10193 | 0.026843 | 5.743% | 11.56% | 27.8% | 27.18% | 1.8 | 0.07613 | 0.020049 | 4.289% | 12.65% | 25.38% | 52.88%
| N4 - L13 | 5.102 | 0 | 1.341 | 2.415 | 18.679 | 4.833 | 2.4 | 0.17295 | 0.04475 | 5.022% | 15.81% | 43.24% | 21.2% | 2.2 | 0.15437 | 0.039942 | 4.482% | 15.85% | 42.1% | 28.01% | 1.8 | 0.1153 | 0.029833 | 3.348% | 16.12% | 38.43% | 54.63%
| N4 - L14 | 8.298 | 0 | 1.374 | 5.986 | 34.209 | 0.02 | 2.4 | 0.31675 | 0.00018519 | 11.16% | 29.86% | 79.19% | 24.24% | 2.2 | 0.28272 | 0.00016529 | 9.965% | 30.2% | 77.11% | 31.83% | 1.8 | 0.21117 | 0.00012346 | 7.443% | 31.67% | 70.39% | 61.03%
| N4 - L15 | 6.52 | 0 | 4.533 | 0.507 | 1.535 | 7.583 | 2.4 | 0.014213 | 0.070213 | 8.292% | 8.474% | 17.55% | 18.95% | 2.2 | 0.012686 | 0.062669 | 7.401% | 9.103% | 17.09% | 25.1% | 1.8 | 0.0094753 | 0.046809 | 5.528% | 11.42% | 15.6% | 49.4%
| N4 - L16 | 9.715 | 0 | 1.819 | 4.078 | 17.065 | 2.73 | 2.4 | 0.15801 | 0.025278 | 8.117% | 15.53% | 39.5% | 21.17% | 2.2 | 0.14103 | 0.022562 | 7.245% | 15.89% | 38.46% | 27.92% | 1.8 | 0.10534 | 0.016852 | 5.412% | 17.3% | 35.11% | 54.24%
| N4 - L17 | 8.181 | 0 | 4.3 | 0.252 | 0.755 | 7.752 | 2.4 | 0.0069907 | 0.071778 | 7.83% | 8.47% | 17.94% | 19.07% | 2.2 | 0.0062397 | 0.064066 | 6.989% | 9.055% | 17.47% | 25.23% | 1.8 | 0.0046605 | 0.047852 | 5.22% | 11.22% | 15.95% | 49.56%
| N4 - L18 | 11.376 | 0 | 1.586 | 3.319 | 14.775 | 2.898 | 2.4 | 0.13681 | 0.026833 | 6.687% | 13.32% | 34.2% | 21% | 2.2 | 0.12211 | 0.02395 | 5.969% | 13.59% | 33.3% | 27.67% | 1.8 | 0.091204 | 0.017889 | 4.458% | 14.69% | 30.4% | 53.75%
| N4 - L19 | 5.102 | 0 | 1.341 | 0 | 0 | 4.833 | 2.4 | 0 | 0.04475 | 2.438% | 4.505% | 11.19% | 18.14% | 2.2 | 0 | 0.039942 | 2.176% | 4.639% | 10.89% | 24.08% | 1.8 | 0 | 0.029833 | 1.625% | 5.154% | 9.944% | 47.63%
| N4 - L20 | 8.298 | 0 | 1.374 | 3.571 | 15.529 | 0.02 | 2.4 | 0.14379 | 0.00018519 | 6.956% | 14.05% | 35.95% | 20.27% | 2.2 | 0.12834 | 0.00016529 | 6.208% | 14.35% | 35% | 26.77% | 1.8 | 0.095858 | 0.00012346 | 4.637% | 15.55% | 31.95% | 52.28%
| N4 - L21 | 6.52 | 0 | 4.533 | 0 | 0 | 7.583 | 2.4 | 0 | 0.070213 | 8.24% | 8.474% | 17.55% | 18.73% | 2.2 | 0 | 0.062669 | 7.355% | 9.103% | 17.09% | 24.81% | 1.8 | 0 | 0.046809 | 5.494% | 11.42% | 15.6% | 48.88%
| N4 - L22 | 9.715 | 0 | 1.819 | 3.571 | 15.529 | 2.73 | 2.4 | 0.14379 | 0.025278 | 7.285% | 14.05% | 35.95% | 20.89% | 2.2 | 0.12834 | 0.022562 | 6.503% | 14.35% | 35% | 27.55% | 1.8 | 0.095858 | 0.016852 | 4.857% | 15.55% | 31.95% | 53.61%
| N4 - L23 | 8.181 | 0 | 4.3 | 0 | 0 | 7.752 | 2.4 | 0 | 0.071778 | 7.817% | 8.47% | 17.94% | 18.96% | 2.2 | 0 | 0.064066 | 6.977% | 9.055% | 17.47% | 25.09% | 1.8 | 0 | 0.047852 | 5.211% | 11.22% | 15.95% | 49.3%
| N4 - L24 | 11.376 | 0 | 1.586 | 3.571 | 15.529 | 2.898 | 2.4 | 0.14379 | 0.026833 | 7.103% | 14.05% | 35.95% | 21.14% | 2.2 | 0.12834 | 0.02395 | 6.34% | 14.35% | 35% | 27.85% | 1.8 | 0.095858 | 0.017889 | 4.735% | 15.55% | 31.95% | 54.06%
| N4 - L25 | 9.123 | 0 | 3.122 | 0 | 0 | 6.006 | 2.4 | 0 | 0.055611 | 5.675% | 6.441% | 13.9% | 18.8% | 2.2 | 0 | 0.049636 | 5.066% | 6.858% | 13.54% | 24.88% | 1.8 | 0 | 0.037074 | 3.784% | 8.402% | 12.36% | 48.89%
| N4 - L26 | 13.589 | 0 | 0.278 | 4.095 | 18.347 | 0.315 | 2.4 | 0.16988 | 0.0029167 | 7.461% | 16.53% | 42.47% | 21.54% | 2.2 | 0.15163 | 0.0026033 | 6.66% | 16.86% | 41.35% | 28.34% | 1.8 | 0.11325 | 0.0019444 | 4.974% | 18.2% | 37.75% | 54.79%
| N4 - L27 | 6.648 | 0 | 3.371 | 0.016 | 0.452 | 6.674 | 2.4 | 0.0041852 | 0.061796 | 6.128% | 7.101% | 15.45% | 18.67% | 2.2 | 0.0037355 | 0.055157 | 5.47% | 7.547% | 15.04% | 24.74% | 1.8 | 0.0027901 | 0.041198 | 4.085% | 9.202% | 13.73% | 48.74%
| N4 - L28 | 10.23 | 0 | 0.485 | 3.555 | 15.982 | 1.416 | 2.4 | 0.14798 | 0.013111 | 6.522% | 14.39% | 37% | 20.83% | 2.2 | 0.13208 | 0.011702 | 5.822% | 14.68% | 36.02% | 27.46% | 1.8 | 0.098654 | 0.0087407 | 4.348% | 15.84% | 32.88% | 53.42%
| N4 - L29 | 4.134 | 0 | 1.323 | 0 | 0 | 5.557 | 2.4 | 0 | 0.051454 | 2.405% | 5.053% | 12.86% | 18.13% | 2.2 | 0 | 0.045926 | 2.147% | 5.169% | 12.53% | 24.07% | 1.8 | 0 | 0.034302 | 1.603% | 5.626% | 11.43% | 47.67%
| N4 - L30 | 7.895 | 0 | 1.707 | 2.941 | 10.415 | 0.036 | 2.4 | 0.096435 | 0.00033333 | 6.182% | 9.738% | 24.11% | 19.35% | 2.2 | 0.086074 | 0.00029752 | 5.517% | 10.03% | 23.47% | 25.6% | 1.8 | 0.06429 | 0.00022222 | 4.121% | 11.18% | 21.43% | 50.22%
| N4 - L31 | 5.951 | 0 | 5.415 | 0 | 0 | 9.082 | 2.4 | 0 | 0.084093 | 9.844% | 10.14% | 21.02% | 18.89% | 2.2 | 0 | 0.075058 | 8.786% | 10.89% | 20.47% | 25.03% | 1.8 | 0 | 0.056062 | 6.562% | 13.66% | 18.69% | 49.3%
| N4 - L32 | 9.712 | 0 | 2.385 | 2.941 | 10.415 | 3.561 | 2.4 | 0.096435 | 0.032972 | 6.883% | 9.738% | 24.11% | 20.12% | 2.2 | 0.086074 | 0.02943 | 6.144% | 10.03% | 23.47% | 26.57% | 1.8 | 0.06429 | 0.021981 | 4.589% | 11.18% | 21.43% | 51.88%
| N4 - L33 | 8.08 | 0 | 5.117 | 0 | 0 | 9.298 | 2.4 | 0 | 0.086093 | 9.302% | 10.14% | 21.52% | 19.19% | 2.2 | 0 | 0.076843 | 8.303% | 10.83% | 20.96% | 25.39% | 1.8 | 0 | 0.057395 | 6.201% | 13.4% | 19.13% | 49.84%
| N4 - L34 | 11.841 | 0 | 2.087 | 2.941 | 10.415 | 3.777 | 2.4 | 0.096435 | 0.034972 | 6.556% | 9.738% | 24.11% | 20.44% | 2.2 | 0.086074 | 0.031215 | 5.851% | 10.03% | 23.47% | 26.94% | 1.8 | 0.06429 | 0.023315 | 4.37% | 11.18% | 21.43% | 52.44%
| N4 - L35 | 4.745 | 0 | 1.365 | 1.263 | 9.786 | 5.316 | 2.4 | 0.090611 | 0.049222 | 3.381% | 8.282% | 22.65% | 19.65% | 2.2 | 0.080876 | 0.043934 | 3.017% | 8.301% | 22.06% | 26.03% | 1.8 | 0.060407 | 0.032815 | 2.254% | 8.444% | 20.14% | 51.15%
| N4 - L36 | 8.303 | 0 | 1.576 | 4.603 | 23.131 | 0.007 | 2.4 | 0.21418 | 6.4815e-05 | 8.844% | 20.51% | 53.54% | 21.71% | 2.2 | 0.19117 | 5.7851e-05 | 7.894% | 20.84% | 52.14% | 28.62% | 1.8 | 0.14278 | 4.321e-05 | 5.896% | 22.18% | 47.59% | 55.52%
| N4 - L37 | 6.398 | 0 | 5.088 | 0.266 | 0.805 | 8.523 | 2.4 | 0.0074537 | 0.078917 | 9.262% | 9.521% | 19.73% | 18.97% | 2.2 | 0.0066529 | 0.070438 | 8.267% | 10.23% | 19.21% | 25.13% | 1.8 | 0.0049691 | 0.052611 | 6.175% | 12.83% | 17.54% | 49.47%
| N4 - L38 | 9.956 | 0 | 2.148 | 3.606 | 14.15 | 3.214 | 2.4 | 0.13102 | 0.029759 | 7.63% | 13.01% | 32.75% | 20.75% | 2.2 | 0.11694 | 0.026562 | 6.81% | 13.34% | 31.89% | 27.37% | 1.8 | 0.087346 | 0.01984 | 5.087% | 14.65% | 29.12% | 53.28%
| N4 - L39 | 8.335 | 0 | 4.817 | 0.132 | 0.396 | 8.719 | 2.4 | 0.0036667 | 0.080731 | 8.76% | 9.515% | 20.18% | 19.19% | 2.2 | 0.0032727 | 0.072058 | 7.819% | 10.17% | 19.65% | 25.38% | 1.8 | 0.0024444 | 0.053821 | 5.84% | 12.59% | 17.94% | 49.82%
| N4 - L40 | 11.893 | 0 | 1.876 | 3.208 | 12.949 | 3.411 | 2.4 | 0.1199 | 0.031583 | 6.756% | 11.85% | 29.97% | 20.83% | 2.2 | 0.10702 | 0.02819 | 6.03% | 12.14% | 29.19% | 27.44% | 1.8 | 0.079932 | 0.021056 | 4.504% | 13.28% | 26.64% | 53.32%
| N4 - L41 | 5.358 | 0 | 1.408 | 2.536 | 19.613 | 5.075 | 2.4 | 0.1816 | 0.046991 | 5.273% | 16.6% | 45.4% | 21.46% | 2.2 | 0.16209 | 0.041942 | 4.706% | 16.64% | 44.21% | 28.33% | 1.8 | 0.12107 | 0.031327 | 3.515% | 16.93% | 40.36% | 55.19%
| N4 - L42 | 8.712 | 0 | 1.442 | 6.285 | 35.919 | 0.021 | 2.4 | 0.33258 | 0.00019444 | 11.72% | 31.35% | 83.15% | 24.74% | 2.2 | 0.29685 | 0.00017355 | 10.46% | 31.71% | 80.96% | 32.46% | 1.8 | 0.22172 | 0.00012963 | 7.815% | 33.26% | 73.91% | 62.1%
| N4 - L43 | 6.846 | 0 | 4.76 | 0.532 | 1.612 | 7.963 | 2.4 | 0.014926 | 0.073731 | 8.707% | 8.899% | 18.43% | 19.06% | 2.2 | 0.013322 | 0.06581 | 7.771% | 9.559% | 17.95% | 25.24% | 1.8 | 0.0099506 | 0.049154 | 5.805% | 11.99% | 16.38% | 49.64%
| N4 - L44 | 10.201 | 0 | 1.91 | 4.282 | 17.918 | 2.866 | 2.4 | 0.16591 | 0.026537 | 8.523% | 16.3% | 41.48% | 21.43% | 2.2 | 0.14808 | 0.023686 | 7.608% | 16.68% | 40.39% | 28.23% | 1.8 | 0.1106 | 0.017691 | 5.682% | 18.16% | 36.87% | 54.77%
| N4 - L45 | 8.59 | 0 | 4.516 | 0.265 | 0.793 | 8.14 | 2.4 | 0.0073426 | 0.07537 | 8.224% | 8.894% | 18.84% | 19.18% | 2.2 | 0.0065537 | 0.067273 | 7.34% | 9.509% | 18.35% | 25.38% | 1.8 | 0.0048951 | 0.050247 | 5.482% | 11.78% | 16.75% | 49.8%
| N4 - L46 | 11.945 | 0 | 1.665 | 3.485 | 15.513 | 3.043 | 2.4 | 0.14364 | 0.028176 | 7.021% | 13.99% | 35.91% | 21.24% | 2.2 | 0.12821 | 0.025149 | 6.267% | 14.27% | 34.97% | 27.97% | 1.8 | 0.095759 | 0.018784 | 4.681% | 15.42% | 31.92% | 54.24%
| N4 - L47 | 5.358 | 0 | 1.408 | 0 | 0 | 5.075 | 2.4 | 0 | 0.046991 | 2.56% | 4.731% | 11.75% | 18.21% | 2.2 | 0 | 0.041942 | 2.285% | 4.871% | 11.44% | 24.16% | 1.8 | 0 | 0.031327 | 1.706% | 5.412% | 10.44% | 47.77%
| N4 - L48 | 8.712 | 0 | 1.442 | 3.749 | 16.306 | 0.021 | 2.4 | 0.15098 | 0.00019444 | 7.302% | 14.75% | 37.75% | 20.46% | 2.2 | 0.13476 | 0.00017355 | 6.517% | 15.07% | 36.75% | 27.01% | 1.8 | 0.10065 | 0.00012963 | 4.868% | 16.33% | 33.55% | 52.69%
| N4 - L49 | 6.846 | 0 | 4.76 | 0 | 0 | 7.963 | 2.4 | 0 | 0.073731 | 8.653% | 8.899% | 18.43% | 18.82% | 2.2 | 0 | 0.06581 | 7.723% | 9.559% | 17.95% | 24.93% | 1.8 | 0 | 0.049154 | 5.769% | 11.99% | 16.38% | 49.09%
| N4 - L50 | 10.201 | 0 | 1.91 | 3.749 | 16.306 | 2.866 | 2.4 | 0.15098 | 0.026537 | 7.649% | 14.75% | 37.75% | 21.12% | 2.2 | 0.13476 | 0.023686 | 6.827% | 15.07% | 36.75% | 27.84% | 1.8 | 0.10065 | 0.017691 | 5.099% | 16.33% | 33.55% | 54.09%
| N4 - L51 | 8.59 | 0 | 4.516 | 0 | 0 | 8.14 | 2.4 | 0 | 0.07537 | 8.209% | 8.894% | 18.84% | 19.07% | 2.2 | 0 | 0.067273 | 7.327% | 9.509% | 18.35% | 25.23% | 1.8 | 0 | 0.050247 | 5.473% | 11.78% | 16.75% | 49.53%
| N4 - L52 | 11.945 | 0 | 1.665 | 3.749 | 16.306 | 3.043 | 2.4 | 0.15098 | 0.028176 | 7.457% | 14.75% | 37.75% | 21.39% | 2.2 | 0.13476 | 0.025149 | 6.656% | 15.07% | 36.75% | 28.16% | 1.8 | 0.10065 | 0.018784 | 4.971% | 16.33% | 33.55% | 54.57%
| N4 - L53 | 12.772 | 0 | 4.371 | 0 | 0 | 8.408 | 2.4 | 0 | 0.077852 | 7.946% | 9.017% | 19.46% | 19.63% | 2.2 | 0 | 0.069488 | 7.092% | 9.601% | 18.95% | 25.9% | 1.8 | 0 | 0.051901 | 5.297% | 11.76% | 17.3% | 50.54%
| N4 - L54 | 19.024 | 0 | 0.389 | 5.733 | 25.686 | 0.44 | 2.4 | 0.23783 | 0.0040741 | 10.45% | 23.14% | 59.46% | 23.87% | 2.2 | 0.21228 | 0.0036364 | 9.323% | 23.61% | 57.89% | 31.23% | 1.8 | 0.15856 | 0.002716 | 6.964% | 25.48% | 52.85% | 59.55%
| N4 - L55 | 7.978 | 0 | 4.045 | 0.019 | 0.543 | 8.009 | 2.4 | 0.0050278 | 0.074157 | 7.353% | 8.521% | 18.54% | 19.05% | 2.2 | 0.0044876 | 0.06619 | 6.563% | 9.056% | 18.05% | 25.21% | 1.8 | 0.0033519 | 0.049438 | 4.902% | 11.04% | 16.48% | 49.54%
| N4 - L56 | 12.276 | 0 | 0.582 | 4.266 | 19.178 | 1.699 | 2.4 | 0.17757 | 0.015731 | 7.827% | 17.27% | 44.39% | 21.76% | 2.2 | 0.1585 | 0.014041 | 6.986% | 17.61% | 43.23% | 28.63% | 1.8 | 0.11838 | 0.010488 | 5.218% | 19.01% | 39.46% | 55.37%
| N5 - L1 | 17.225 | 0 | 8.543 | 0 | 0 | 12.502 | 2.4 | 0 | 0.11576 | 15.53% | 14.59% | 28.94% | 20.88% | 2.2 | 0 | 0.10332 | 13.86% | 15.81% | 28.18% | 27.45% | 1.8 | 0 | 0.077173 | 10.35% | 20.29% | 25.72% | 53.1%
| N5 - L2 | 17.225 | 0 | 3.755 | 3.841 | 13.035 | 5.358 | 2.4 | 0.12069 | 0.049611 | 9.765% | 12.28% | 30.17% | 21.88% | 2.2 | 0.10773 | 0.044281 | 8.716% | 12.68% | 29.38% | 28.73% | 1.8 | 0.080463 | 0.033074 | 6.51% | 14.21% | 26.82% | 55.34%
| N5 - L3 | 13.466 | 0 | 4.361 | 0 | 0 | 7.864 | 2.4 | 0 | 0.072815 | 7.928% | 8.592% | 18.2% | 19.62% | 2.2 | 0 | 0.064992 | 7.076% | 9.185% | 17.73% | 25.88% | 1.8 | 0 | 0.048543 | 5.285% | 11.38% | 16.18% | 50.49%
| N5 - L4 | 13.466 | 0 | 0.427 | 3.841 | 13.035 | 0.719 | 2.4 | 0.12069 | 0.0066574 | 7.025% | 12.28% | 30.17% | 20.61% | 2.2 | 0.10773 | 0.0059421 | 6.271% | 12.68% | 29.38% | 27.15% | 1.8 | 0.080463 | 0.0044383 | 4.684% | 14.21% | 26.82% | 52.72%
| N5 - L5 | 9.708 | 0 | 8.543 | 0 | 0 | 12.502 | 2.4 | 0 | 0.11576 | 15.53% | 14.59% | 28.94% | 19.92% | 2.2 | 0 | 0.10332 | 13.86% | 15.81% | 28.18% | 26.31% | 1.8 | 0 | 0.077173 | 10.35% | 20.29% | 25.72% | 51.41%
| N5 - L6 | 9.708 | 0 | 3.755 | 3.841 | 13.035 | 5.358 | 2.4 | 0.12069 | 0.049611 | 9.765% | 12.28% | 30.17% | 20.87% | 2.2 | 0.10773 | 0.044281 | 8.716% | 12.68% | 29.38% | 27.53% | 1.8 | 0.080463 | 0.033074 | 6.51% | 14.21% | 26.82% | 53.58%
| N5 - L7 | 16.886 | 0 | 8.009 | 0.253 | 0.766 | 11.705 | 2.4 | 0.0070926 | 0.10838 | 14.57% | 13.67% | 27.09% | 20.82% | 2.2 | 0.0063306 | 0.096736 | 13% | 14.81% | 26.38% | 27.38% | 1.8 | 0.0047284 | 0.072253 | 9.711% | 19.01% | 24.08% | 52.98%
| N5 - L8 | 16.886 | 0 | 3.41 | 4.474 | 16.591 | 4.865 | 2.4 | 0.15362 | 0.045046 | 10.23% | 15.39% | 38.41% | 22.44% | 2.2 | 0.13712 | 0.040207 | 9.127% | 15.83% | 37.4% | 29.44% | 1.8 | 0.10241 | 0.030031 | 6.817% | 17.52% | 34.14% | 56.59%
| N5 - L9 | 13.466 | 0 | 4.205 | 0.824 | 8.177 | 7.485 | 2.4 | 0.075713 | 0.069306 | 7.789% | 8.209% | 18.93% | 20.88% | 2.2 | 0.067579 | 0.06186 | 6.953% | 8.783% | 18.43% | 27.5% | 1.8 | 0.050475 | 0.046204 | 5.193% | 10.9% | 16.83% | 53.35%
| N5 - L10 | 13.466 | 0 | 0.395 | 5.045 | 24.003 | 0.644 | 2.4 | 0.22225 | 0.005963 | 9.199% | 21.44% | 55.56% | 22.74% | 2.2 | 0.19837 | 0.0053223 | 8.211% | 21.82% | 54.1% | 29.86% | 1.8 | 0.14817 | 0.0039753 | 6.133% | 23.38% | 49.39% | 57.44%
| N5 - L11 | 10.047 | 0 | 8.009 | 0.253 | 0.766 | 11.705 | 2.4 | 0.0070926 | 0.10838 | 14.57% | 13.67% | 27.09% | 19.95% | 2.2 | 0.0063306 | 0.096736 | 13% | 14.81% | 26.38% | 26.34% | 1.8 | 0.0047284 | 0.072253 | 9.711% | 19.01% | 24.08% | 51.45%
| N5 - L12 | 10.047 | 0 | 3.41 | 4.474 | 16.592 | 4.865 | 2.4 | 0.15363 | 0.045046 | 10.23% | 15.39% | 38.41% | 21.49% | 2.2 | 0.13712 | 0.040207 | 9.127% | 15.83% | 37.4% | 28.32% | 1.8 | 0.10242 | 0.030031 | 6.817% | 17.52% | 34.14% | 54.94%
| N5 - L13 | 16.545 | 0 | 7.475 | 0.507 | 1.535 | 10.907 | 2.4 | 0.014213 | 0.10099 | 13.62% | 12.74% | 25.25% | 20.76% | 2.2 | 0.012686 | 0.09014 | 12.16% | 13.81% | 24.58% | 27.31% | 1.8 | 0.0094753 | 0.067327 | 9.08% | 17.73% | 22.44% | 52.87%
| N5 - L14 | 16.545 | 0 | 3.064 | 5.118 | 20.181 | 4.37 | 2.4 | 0.18686 | 0.040463 | 10.84% | 18.53% | 46.72% | 23.03% | 2.2 | 0.16679 | 0.036116 | 9.679% | 19.01% | 45.49% | 30.2% | 1.8 | 0.12457 | 0.026975 | 7.229% | 20.86% | 41.52% | 57.92%
| N5 - L15 | 13.466 | 0 | 4.05 | 1.656 | 16.389 | 7.107 | 2.4 | 0.15175 | 0.065806 | 7.954% | 13.6% | 37.94% | 22.33% | 2.2 | 0.13545 | 0.058736 | 7.099% | 13.56% | 36.94% | 29.34% | 1.8 | 0.10117 | 0.04387 | 5.303% | 13.51% | 33.72% | 56.58%
| N5 - L16 | 13.466 | 0 | 0.361 | 6.267 | 35.034 | 0.571 | 2.4 | 0.32439 | 0.005287 | 11.41% | 30.66% | 81.1% | 25.37% | 2.2 | 0.28954 | 0.004719 | 10.19% | 31.03% | 78.96% | 33.2% | 1.8 | 0.21626 | 0.0035247 | 7.608% | 32.63% | 72.09% | 63.13%
| N5 - L17 | 10.388 | 0 | 7.475 | 0.507 | 1.535 | 10.907 | 2.4 | 0.014213 | 0.10099 | 13.62% | 12.74% | 25.25% | 19.98% | 2.2 | 0.012686 | 0.09014 | 12.16% | 13.81% | 24.58% | 26.37% | 1.8 | 0.0094753 | 0.067327 | 9.08% | 17.73% | 22.44% | 51.49%
| N5 - L18 | 10.388 | 0 | 3.064 | 5.118 | 20.181 | 4.37 | 2.4 | 0.18686 | 0.040463 | 10.84% | 18.53% | 46.72% | 22.16% | 2.2 | 0.16679 | 0.036116 | 9.679% | 19.01% | 45.49% | 29.17% | 1.8 | 0.12457 | 0.026975 | 7.229% | 20.86% | 41.52% | 56.4%
| N5 - L19 | 16.545 | 0 | 7.475 | 0 | 0 | 10.907 | 2.4 | 0 | 0.10099 | 13.59% | 12.74% | 25.25% | 20.52% | 2.2 | 0 | 0.09014 | 12.13% | 13.81% | 24.58% | 26.99% | 1.8 | 0 | 0.067327 | 9.059% | 17.73% | 22.44% | 52.32%
| N5 - L20 | 16.545 | 0 | 3.064 | 4.611 | 18.645 | 4.37 | 2.4 | 0.17264 | 0.040463 | 10.06% | 17.05% | 43.16% | 22.71% | 2.2 | 0.15409 | 0.036116 | 8.983% | 17.47% | 42.02% | 29.79% | 1.8 | 0.11509 | 0.026975 | 6.709% | 19.11% | 38.36% | 57.22%
| N5 - L21 | 13.466 | 0 | 4.05 | 0 | 0 | 7.107 | 2.4 | 0 | 0.065806 | 7.362% | 7.828% | 16.45% | 19.5% | 2.2 | 0 | 0.058736 | 6.571% | 8.382% | 16.02% | 25.73% | 1.8 | 0 | 0.04387 | 4.908% | 10.43% | 14.62% | 50.22%
| N5 - L22 | 13.466 | 0 | 0.361 | 4.611 | 18.645 | 0.571 | 2.4 | 0.17264 | 0.005287 | 8.408% | 17.05% | 43.16% | 21.63% | 2.2 | 0.15409 | 0.004719 | 7.504% | 17.47% | 42.02% | 28.44% | 1.8 | 0.11509 | 0.0035247 | 5.605% | 19.11% | 38.36% | 54.99%
| N5 - L23 | 10.388 | 0 | 7.475 | 0 | 0 | 10.907 | 2.4 | 0 | 0.10099 | 13.59% | 12.74% | 25.25% | 19.74% | 2.2 | 0 | 0.09014 | 12.13% | 13.81% | 24.58% | 26.07% | 1.8 | 0 | 0.067327 | 9.059% | 17.73% | 22.44% | 50.95%
| N5 - L24 | 10.388 | 0 | 3.064 | 4.611 | 18.645 | 4.37 | 2.4 | 0.17264 | 0.040463 | 10.06% | 17.05% | 43.16% | 21.85% | 2.2 | 0.15409 | 0.036116 | 8.983% | 17.47% | 42.02% | 28.77% | 1.8 | 0.11509 | 0.026975 | 6.709% | 19.11% | 38.36% | 55.72%
| N5 - L25 | 15.631 | 0 | 5.703 | 0 | 0 | 8.565 | 2.4 | 0 | 0.079306 | 10.37% | 9.909% | 19.83% | 20.01% | 2.2 | 0 | 0.070785 | 9.253% | 10.72% | 19.31% | 26.35% | 1.8 | 0 | 0.05287 | 6.911% | 13.7% | 17.62% | 51.23%
| N5 - L26 | 15.631 | 0 | 0.068 | 5.243 | 21.785 | 0.108 | 2.4 | 0.20171 | 0.001 | 9.532% | 19.84% | 50.43% | 22.48% | 2.2 | 0.18004 | 0.00089256 | 8.508% | 20.31% | 49.1% | 29.5% | 1.8 | 0.13448 | 0.00066667 | 6.355% | 22.13% | 44.83% | 56.73%
| N5 - L27 | 13.465 | 0 | 6.286 | 0.032 | 0.597 | 9.565 | 2.4 | 0.0055278 | 0.088565 | 11.43% | 11.02% | 22.14% | 19.99% | 2.2 | 0.0049339 | 0.07905 | 10.2% | 11.91% | 21.56% | 26.36% | 1.8 | 0.0036852 | 0.059043 | 7.618% | 15.18% | 19.68% | 51.33%
| N5 - L28 | 13.465 | 0 | 1.498 | 4.643 | 19.242 | 2.42 | 2.4 | 0.17817 | 0.022407 | 8.869% | 17.53% | 44.54% | 22.06% | 2.2 | 0.15902 | 0.02 | 7.916% | 17.95% | 43.37% | 29% | 1.8 | 0.11878 | 0.014938 | 5.912% | 19.57% | 39.59% | 55.96%
| N5 - L29 | 18.086 | 0 | 8.97 | 0 | 0 | 13.127 | 2.4 | 0 | 0.12155 | 16.31% | 15.32% | 30.39% | 21.11% | 2.2 | 0 | 0.10849 | 14.55% | 16.6% | 29.59% | 27.73% | 1.8 | 0 | 0.081031 | 10.87% | 21.31% | 27.01% | 53.54%
| N5 - L30 | 18.086 | 0 | 3.942 | 4.033 | 13.687 | 5.625 | 2.4 | 0.12673 | 0.052083 | 10.25% | 12.89% | 31.68% | 22.17% | 2.2 | 0.11312 | 0.046488 | 9.15% | 13.31% | 30.85% | 29.08% | 1.8 | 0.084488 | 0.034722 | 6.835% | 14.92% | 28.16% | 55.93%
| N5 - L31 | 14.14 | 0 | 4.579 | 0 | 0 | 8.257 | 2.4 | 0 | 0.076454 | 8.324% | 9.021% | 19.11% | 19.77% | 2.2 | 0 | 0.06824 | 7.43% | 9.644% | 18.61% | 26.06% | 1.8 | 0 | 0.050969 | 5.549% | 11.94% | 16.99% | 50.79%
| N5 - L32 | 14.14 | 0 | 0.448 | 4.033 | 13.687 | 0.755 | 2.4 | 0.12673 | 0.0069907 | 7.377% | 12.89% | 31.68% | 20.82% | 2.2 | 0.11312 | 0.0062397 | 6.584% | 13.31% | 30.85% | 27.41% | 1.8 | 0.084488 | 0.0046605 | 4.918% | 14.92% | 28.16% | 53.15%
| N5 - L33 | 10.194 | 0 | 8.97 | 0 | 0 | 13.127 | 2.4 | 0 | 0.12155 | 16.31% | 15.32% | 30.39% | 20.09% | 2.2 | 0 | 0.10849 | 14.55% | 16.6% | 29.59% | 26.52% | 1.8 | 0 | 0.081031 | 10.87% | 21.31% | 27.01% | 51.76%
| N5 - L34 | 10.194 | 0 | 3.942 | 4.033 | 13.687 | 5.625 | 2.4 | 0.12673 | 0.052083 | 10.25% | 12.89% | 31.68% | 21.1% | 2.2 | 0.11312 | 0.046488 | 9.15% | 13.31% | 30.85% | 27.82% | 1.8 | 0.084488 | 0.034722 | 6.835% | 14.92% | 28.16% | 54.06%
| N5 - L35 | 17.73 | 0 | 8.41 | 0.266 | 0.805 | 12.291 | 2.4 | 0.0074537 | 0.11381 | 15.3% | 14.35% | 28.45% | 21.04% | 2.2 | 0.0066529 | 0.10158 | 13.65% | 15.55% | 27.7% | 27.65% | 1.8 | 0.0049691 | 0.07587 | 10.2% | 19.97% | 25.29% | 53.42%
| N5 - L36 | 17.73 | 0 | 3.58 | 4.698 | 17.421 | 5.108 | 2.4 | 0.16131 | 0.047296 | 10.74% | 16.16% | 40.33% | 22.76% | 2.2 | 0.14398 | 0.042215 | 9.584% | 16.62% | 39.27% | 29.84% | 1.8 | 0.10754 | 0.031531 | 7.158% | 18.39% | 35.85% | 57.26%
| N5 - L37 | 14.14 | 0 | 4.415 | 0.865 | 8.586 | 7.859 | 2.4 | 0.0795 | 0.072769 | 8.178% | 8.619% | 19.88% | 21.1% | 2.2 | 0.070959 | 0.06495 | 7.3% | 9.222% | 19.35% | 27.77% | 1.8 | 0.053 | 0.048512 | 5.452% | 11.45% | 17.67% | 53.81%
| N5 - L38 | 14.14 | 0 | 0.414 | 5.297 | 25.203 | 0.677 | 2.4 | 0.23336 | 0.0062685 | 9.659% | 22.51% | 58.34% | 23.1% | 2.2 | 0.20829 | 0.005595 | 8.621% | 22.92% | 56.81% | 30.31% | 1.8 | 0.15557 | 0.004179 | 6.439% | 24.55% | 51.86% | 58.19%
| N5 - L39 | 10.55 | 0 | 8.41 | 0.266 | 0.805 | 12.291 | 2.4 | 0.0074537 | 0.11381 | 15.3% | 14.35% | 28.45% | 20.12% | 2.2 | 0.0066529 | 0.10158 | 13.65% | 15.55% | 27.7% | 26.55% | 1.8 | 0.0049691 | 0.07587 | 10.2% | 19.97% | 25.29% | 51.8%
| N5 - L40 | 10.55 | 0 | 3.58 | 4.698 | 17.421 | 5.108 | 2.4 | 0.16131 | 0.047296 | 10.74% | 16.16% | 40.33% | 21.76% | 2.2 | 0.14398 | 0.042215 | 9.584% | 16.62% | 39.27% | 28.66% | 1.8 | 0.10754 | 0.031531 | 7.158% | 18.39% | 35.85% | 55.52%
| N5 - L41 | 17.372 | 0 | 7.849 | 0.532 | 1.612 | 11.452 | 2.4 | 0.014926 | 0.10604 | 14.3% | 13.38% | 26.51% | 20.98% | 2.2 | 0.013322 | 0.094645 | 12.76% | 14.5% | 25.81% | 27.57% | 1.8 | 0.0099506 | 0.070691 | 9.534% | 18.62% | 23.56% | 53.3%
| N5 - L42 | 17.372 | 0 | 3.217 | 5.374 | 21.19 | 4.589 | 2.4 | 0.1962 | 0.042491 | 11.39% | 19.46% | 49.05% | 23.41% | 2.2 | 0.17512 | 0.037926 | 10.16% | 19.96% | 47.76% | 30.66% | 1.8 | 0.1308 | 0.028327 | 7.591% | 21.91% | 43.6% | 58.68%
| N5 - L43 | 14.14 | 0 | 4.252 | 1.739 | 17.209 | 7.463 | 2.4 | 0.15934 | 0.069102 | 8.351% | 14.28% | 39.84% | 22.65% | 2.2 | 0.14222 | 0.061678 | 7.454% | 14.24% | 38.79% | 29.75% | 1.8 | 0.10623 | 0.046068 | 5.567% | 14.19% | 35.41% | 57.25%
| N5 - L44 | 14.14 | 0 | 0.379 | 6.581 | 36.786 | 0.599 | 2.4 | 0.34061 | 0.0055463 | 11.98% | 32.19% | 85.15% | 25.97% | 2.2 | 0.30402 | 0.0049504 | 10.7% | 32.58% | 82.91% | 33.94% | 1.8 | 0.22707 | 0.0036975 | 7.989% | 34.26% | 75.69% | 64.34%
| N5 - L45 | 10.907 | 0 | 7.849 | 0.532 | 1.612 | 11.452 | 2.4 | 0.014926 | 0.10604 | 14.3% | 13.38% | 26.51% | 20.15% | 2.2 | 0.013322 | 0.094645 | 12.76% | 14.5% | 25.81% | 26.58% | 1.8 | 0.0099506 | 0.070691 | 9.534% | 18.62% | 23.56% | 51.84%
| N5 - L46 | 10.907 | 0 | 3.217 | 5.374 | 21.19 | 4.589 | 2.4 | 0.1962 | 0.042491 | 11.39% | 19.46% | 49.05% | 22.48% | 2.2 | 0.17512 | 0.037926 | 10.16% | 19.96% | 47.76% | 29.57% | 1.8 | 0.1308 | 0.028327 | 7.591% | 21.91% | 43.6% | 57.07%
| N5 - L47 | 17.372 | 0 | 7.849 | 0 | 0 | 11.452 | 2.4 | 0 | 0.10604 | 14.27% | 13.38% | 26.51% | 20.72% | 2.2 | 0 | 0.094645 | 12.74% | 14.5% | 25.81% | 27.24% | 1.8 | 0 | 0.070691 | 9.512% | 18.62% | 23.56% | 52.72%
| N5 - L48 | 17.372 | 0 | 3.217 | 4.842 | 19.577 | 4.589 | 2.4 | 0.18127 | 0.042491 | 10.57% | 17.91% | 45.32% | 23.06% | 2.2 | 0.16179 | 0.037926 | 9.432% | 18.35% | 44.13% | 30.23% | 1.8 | 0.12085 | 0.028327 | 7.045% | 20.07% | 40.28% | 57.93%
| N5 - L49 | 14.14 | 0 | 4.252 | 0 | 0 | 7.463 | 2.4 | 0 | 0.069102 | 7.73% | 8.219% | 17.28% | 19.64% | 2.2 | 0 | 0.061678 | 6.899% | 8.802% | 16.82% | 25.9% | 1.8 | 0 | 0.046068 | 5.153% | 10.95% | 15.36% | 50.49%
| N5 - L50 | 14.14 | 0 | 0.379 | 4.842 | 19.577 | 0.599 | 2.4 | 0.18127 | 0.0055463 | 8.829% | 17.91% | 45.32% | 21.91% | 2.2 | 0.16179 | 0.0049504 | 7.88% | 18.35% | 44.13% | 28.79% | 1.8 | 0.12085 | 0.0036975 | 5.886% | 20.07% | 40.28% | 55.57%
| N5 - L51 | 10.907 | 0 | 7.849 | 0 | 0 | 11.452 | 2.4 | 0 | 0.10604 | 14.27% | 13.38% | 26.51% | 19.9% | 2.2 | 0 | 0.094645 | 12.74% | 14.5% | 25.81% | 26.26% | 1.8 | 0 | 0.070691 | 9.512% | 18.62% | 23.56% | 51.27%
| N5 - L52 | 10.907 | 0 | 3.217 | 4.842 | 19.578 | 4.589 | 2.4 | 0.18128 | 0.042491 | 10.57% | 17.91% | 45.32% | 22.15% | 2.2 | 0.1618 | 0.037926 | 9.432% | 18.35% | 44.13% | 29.15% | 1.8 | 0.12085 | 0.028327 | 7.045% | 20.07% | 40.28% | 56.35%
| N5 - L53 | 21.884 | 0 | 7.984 | 0 | 0 | 11.991 | 2.4 | 0 | 0.11103 | 14.51% | 13.87% | 27.76% | 21.39% | 2.2 | 0 | 0.099099 | 12.95% | 15.01% | 27.03% | 28.04% | 1.8 | 0 | 0.074019 | 9.676% | 19.18% | 24.67% | 53.94%
| N5 - L54 | 21.884 | 0 | 0.096 | 7.34 | 30.499 | 0.151 | 2.4 | 0.2824 | 0.0013981 | 13.34% | 27.78% | 70.6% | 25.41% | 2.2 | 0.25206 | 0.0012479 | 11.91% | 28.43% | 68.74% | 33.14% | 1.8 | 0.18827 | 0.0009321 | 8.896% | 30.99% | 62.76% | 62.66%
| N5 - L55 | 16.157 | 0 | 7.544 | 0.039 | 0.716 | 11.478 | 2.4 | 0.0066296 | 0.10628 | 13.71% | 13.22% | 26.57% | 20.68% | 2.2 | 0.0059174 | 0.09486 | 12.24% | 14.29% | 25.87% | 27.21% | 1.8 | 0.0044198 | 0.070852 | 9.143% | 18.22% | 23.62% | 52.71%
| N5 - L56 | 16.157 | 0 | 1.798 | 5.572 | 23.091 | 2.904 | 2.4 | 0.21381 | 0.026889 | 10.64% | 21.04% | 53.45% | 23.33% | 2.2 | 0.19083 | 0.024 | 9.5% | 21.53% | 52.05% | 30.58% | 1.8 | 0.14254 | 0.017926 | 7.096% | 23.48% | 47.51% | 58.58%
| N6 - L1 | 16.975 | 0 | 5.407 | 0 | 0 | 9.266 | 2.4 | 0 | 0.085796 | 9.829% | 10.28% | 21.45% | 20.29% | 2.2 | 0 | 0.076579 | 8.773% | 11.02% | 20.89% | 26.7% | 1.8 | 0 | 0.057198 | 6.553% | 13.77% | 19.07% | 51.78%
| N6 - L2 | 13.394 | 0 | 2.521 | 2.943 | 10.114 | 4.008 | 2.4 | 0.093648 | 0.037111 | 7.044% | 9.507% | 23.41% | 20.62% | 2.2 | 0.083587 | 0.033124 | 6.288% | 9.81% | 22.8% | 27.16% | 1.8 | 0.062432 | 0.024741 | 4.696% | 10.97% | 20.81% | 52.77%
| N6 - L3 | 19.003 | 0 | 5.691 | 0 | 0 | 9.06 | 2.4 | 0 | 0.083889 | 10.35% | 10.28% | 20.97% | 20.51% | 2.2 | 0 | 0.074876 | 9.234% | 11.08% | 20.42% | 26.95% | 1.8 | 0 | 0.055926 | 6.897% | 14.02% | 18.64% | 52.15%
| N6 - L4 | 15.421 | 0 | 2.805 | 2.943 | 10.114 | 3.802 | 2.4 | 0.093648 | 0.035204 | 7.391% | 9.507% | 23.41% | 20.85% | 2.2 | 0.083587 | 0.031421 | 6.597% | 9.81% | 22.8% | 27.43% | 1.8 | 0.062432 | 0.023469 | 4.927% | 10.97% | 20.81% | 53.15%
| N6 - L5 | 20.733 | 0 | 1.794 | 0 | 0 | 5.703 | 2.4 | 0 | 0.052806 | 3.261% | 5.439% | 13.2% | 20.16% | 2.2 | 0 | 0.047132 | 2.911% | 5.633% | 12.85% | 26.49% | 1.8 | 0 | 0.035204 | 2.174% | 6.372% | 11.73% | 51.27%
| N6 - L6 | 17.152 | 0 | 1.092 | 2.943 | 10.114 | 0.445 | 2.4 | 0.093648 | 0.0041204 | 5.706% | 9.507% | 23.41% | 20.53% | 2.2 | 0.083587 | 0.0036777 | 5.093% | 9.81% | 22.8% | 27% | 1.8 | 0.062432 | 0.0027469 | 3.804% | 10.97% | 20.81% | 52.31%
| N6 - L7 | 16.732 | 0 | 5.121 | 0.126 | 0.377 | 8.715 | 2.4 | 0.0034907 | 0.080694 | 9.312% | 9.688% | 20.17% | 20.23% | 2.2 | 0.0031157 | 0.072025 | 8.312% | 10.4% | 19.64% | 26.62% | 1.8 | 0.0023272 | 0.053796 | 6.208% | 13% | 17.93% | 51.66%
| N6 - L8 | 13.344 | 0 | 2.321 | 3.197 | 12.527 | 3.659 | 2.4 | 0.11599 | 0.03388 | 7.182% | 11.52% | 29% | 20.98% | 2.2 | 0.10353 | 0.03024 | 6.41% | 11.81% | 28.24% | 27.63% | 1.8 | 0.077327 | 0.022586 | 4.788% | 12.98% | 25.78% | 53.58%
| N6 - L9 | 18.577 | 0 | 5.379 | 0.253 | 0.766 | 8.528 | 2.4 | 0.0070926 | 0.078963 | 9.789% | 9.693% | 19.74% | 20.49% | 2.2 | 0.0063306 | 0.070479 | 8.737% | 10.45% | 19.22% | 26.93% | 1.8 | 0.0047284 | 0.052642 | 6.526% | 13.23% | 17.55% | 52.13%
| N6 - L10 | 15.189 | 0 | 2.579 | 3.576 | 13.67 | 3.472 | 2.4 | 0.12657 | 0.032148 | 8.015% | 12.62% | 31.64% | 21.4% | 2.2 | 0.11298 | 0.028694 | 7.154% | 12.96% | 30.81% | 28.14% | 1.8 | 0.084383 | 0.021432 | 5.343% | 14.28% | 28.13% | 54.4%
| N6 - L11 | 20.152 | 0 | 1.833 | 1.203 | 9.32 | 5.473 | 2.4 | 0.086296 | 0.050676 | 3.986% | 7.888% | 21.57% | 21.61% | 2.2 | 0.077025 | 0.045231 | 3.557% | 7.906% | 21.01% | 28.34% | 1.8 | 0.057531 | 0.033784 | 2.657% | 8.043% | 19.18% | 54.55%
| N6 - L12 | 16.763 | 0 | 0.967 | 4.526 | 22.224 | 0.417 | 2.4 | 0.20578 | 0.0038611 | 8.413% | 19.77% | 51.44% | 22.78% | 2.2 | 0.18367 | 0.0034463 | 7.509% | 20.1% | 50.09% | 29.88% | 1.8 | 0.13719 | 0.0025741 | 5.609% | 21.45% | 45.73% | 57.33%
| N6 - L13 | 16.49 | 0 | 4.834 | 0.252 | 0.755 | 8.163 | 2.4 | 0.0069907 | 0.075583 | 8.799% | 9.096% | 18.9% | 20.16% | 2.2 | 0.0062397 | 0.067463 | 7.854% | 9.765% | 18.4% | 26.54% | 1.8 | 0.0046605 | 0.050389 | 5.866% | 12.23% | 16.8% | 51.53%
| N6 - L14 | 13.295 | 0 | 2.12 | 3.461 | 14.969 | 3.309 | 2.4 | 0.1386 | 0.030639 | 7.378% | 13.55% | 34.65% | 21.36% | 2.2 | 0.12371 | 0.027347 | 6.585% | 13.85% | 33.74% | 28.11% | 1.8 | 0.092401 | 0.020426 | 4.919% | 15.01% | 30.8% | 54.43%
| N6 - L15 | 18.151 | 0 | 5.067 | 0.507 | 1.535 | 7.994 | 2.4 | 0.014213 | 0.074019 | 9.257% | 9.101% | 18.5% | 20.47% | 2.2 | 0.012686 | 0.066066 | 8.263% | 9.813% | 18.02% | 26.91% | 1.8 | 0.0094753 | 0.049346 | 6.171% | 12.43% | 16.45% | 52.11%
| N6 - L16 | 14.956 | 0 | 2.353 | 4.22 | 17.259 | 3.141 | 2.4 | 0.15981 | 0.029083 | 8.783% | 15.76% | 39.95% | 22% | 2.2 | 0.14264 | 0.025959 | 7.84% | 16.14% | 38.9% | 28.9% | 1.8 | 0.10654 | 0.019389 | 5.856% | 17.63% | 35.51% | 55.73%
| N6 - L17 | 19.568 | 0 | 1.874 | 2.415 | 18.679 | 5.244 | 2.4 | 0.17295 | 0.048556 | 5.557% | 15.81% | 43.24% | 23.31% | 2.2 | 0.15437 | 0.043339 | 4.96% | 15.85% | 42.1% | 30.51% | 1.8 | 0.1153 | 0.03237 | 3.705% | 16.12% | 38.43% | 58.33%
| N6 - L18 | 16.373 | 0 | 0.84 | 6.128 | 34.403 | 0.39 | 2.4 | 0.31855 | 0.0036111 | 11.24% | 30.09% | 79.64% | 25.63% | 2.2 | 0.28432 | 0.0032231 | 10.04% | 30.45% | 77.54% | 33.48% | 1.8 | 0.21236 | 0.0024074 | 7.496% | 32% | 70.79% | 63.48%
| N6 - L19 | 16.49 | 0 | 4.834 | 0 | 0 | 8.163 | 2.4 | 0 | 0.075583 | 8.788% | 9.096% | 18.9% | 20.05% | 2.2 | 0 | 0.067463 | 7.843% | 9.765% | 18.4% | 26.39% | 1.8 | 0 | 0.050389 | 5.858% | 12.23% | 16.8% | 51.26%
| N6 - L20 | 13.295 | 0 | 2.12 | 3.713 | 15.724 | 3.309 | 2.4 | 0.14559 | 0.030639 | 7.772% | 14.28% | 36.4% | 21.51% | 2.2 | 0.12995 | 0.027347 | 6.937% | 14.6% | 35.44% | 28.29% | 1.8 | 0.097062 | 0.020426 | 5.182% | 15.88% | 32.35% | 54.75%
| N6 - L21 | 18.151 | 0 | 5.067 | 0 | 0 | 7.994 | 2.4 | 0 | 0.074019 | 9.211% | 9.101% | 18.5% | 20.22% | 2.2 | 0 | 0.066066 | 8.221% | 9.813% | 18.02% | 26.6% | 1.8 | 0 | 0.049346 | 6.141% | 12.43% | 16.45% | 51.56%
| N6 - L22 | 14.956 | 0 | 2.352 | 3.713 | 15.724 | 3.14 | 2.4 | 0.14559 | 0.029074 | 7.99% | 14.28% | 36.4% | 21.7% | 2.2 | 0.12995 | 0.02595 | 7.132% | 14.6% | 35.44% | 28.52% | 1.8 | 0.097062 | 0.019383 | 5.327% | 15.88% | 32.35% | 55.08%
| N6 - L23 | 19.568 | 0 | 1.874 | 0 | 0 | 5.244 | 2.4 | 0 | 0.048556 | 3.407% | 5.131% | 12.14% | 19.95% | 2.2 | 0 | 0.043339 | 3.041% | 5.348% | 11.82% | 26.23% | 1.8 | 0 | 0.03237 | 2.271% | 6.167% | 10.79% | 50.86%
| N6 - L24 | 16.373 | 0 | 0.84 | 3.713 | 15.724 | 0.39 | 2.4 | 0.14559 | 0.0036111 | 6.92% | 14.28% | 36.4% | 21.43% | 2.2 | 0.12995 | 0.0032231 | 6.177% | 14.6% | 35.44% | 28.15% | 1.8 | 0.097062 | 0.0024074 | 4.614% | 15.88% | 32.35% | 54.36%
| N6 - L25 | 19.134 | 0 | 3.745 | 0 | 0 | 6.502 | 2.4 | 0 | 0.060204 | 6.808% | 7.184% | 15.05% | 20.1% | 2.2 | 0 | 0.053736 | 6.076% | 7.699% | 14.66% | 26.43% | 1.8 | 0 | 0.040136 | 4.539% | 9.597% | 13.38% | 51.22%
| N6 - L26 | 14.669 | 0 | 0.346 | 4.25 | 18.559 | 0.181 | 2.4 | 0.17184 | 0.0016759 | 7.751% | 16.78% | 42.96% | 21.71% | 2.2 | 0.15338 | 0.0014959 | 6.919% | 17.14% | 41.83% | 28.53% | 1.8 | 0.11456 | 0.0011173 | 5.168% | 18.56% | 38.19% | 55.09%
| N6 - L27 | 18.024 | 0 | 3.903 | 0.016 | 1.951 | 7.083 | 2.4 | 0.018065 | 0.065583 | 7.095% | 7.724% | 16.4% | 20.36% | 2.2 | 0.016124 | 0.058537 | 6.333% | 8.254% | 15.96% | 26.78% | 1.8 | 0.012043 | 0.043722 | 4.73% | 10.21% | 14.57% | 51.89%
| N6 - L28 | 14.443 | 0 | 1.017 | 3.697 | 17.674 | 1.824 | 2.4 | 0.16365 | 0.016889 | 6.97% | 15.78% | 40.91% | 21.78% | 2.2 | 0.14607 | 0.015074 | 6.221% | 16.06% | 39.84% | 28.63% | 1.8 | 0.1091 | 0.011259 | 4.647% | 17.19% | 36.37% | 55.28%
| N6 - L29 | 17.824 | 0 | 5.678 | 0 | 0 | 9.73 | 2.4 | 0 | 0.090093 | 10.32% | 10.79% | 22.52% | 20.48% | 2.2 | 0 | 0.080413 | 9.213% | 11.58% | 21.93% | 26.92% | 1.8 | 0 | 0.060062 | 6.881% | 14.46% | 20.02% | 52.15%
| N6 - L30 | 14.063 | 0 | 2.647 | 3.09 | 10.619 | 4.208 | 2.4 | 0.098324 | 0.038963 | 7.396% | 9.982% | 24.58% | 20.83% | 2.2 | 0.08776 | 0.034777 | 6.602% | 10.3% | 23.93% | 27.42% | 1.8 | 0.065549 | 0.025975 | 4.931% | 11.52% | 21.85% | 53.19%
| N6 - L31 | 19.953 | 0 | 5.976 | 0 | 0 | 9.513 | 2.4 | 0 | 0.088083 | 10.86% | 10.8% | 22.02% | 20.7% | 2.2 | 0 | 0.07862 | 9.696% | 11.64% | 21.44% | 27.19% | 1.8 | 0 | 0.058722 | 7.242% | 14.72% | 19.57% | 52.53%
| N6 - L32 | 16.193 | 0 | 2.946 | 3.09 | 10.619 | 3.992 | 2.4 | 0.098324 | 0.036963 | 7.761% | 9.982% | 24.58% | 21.07% | 2.2 | 0.08776 | 0.032992 | 6.927% | 10.3% | 23.93% | 27.71% | 1.8 | 0.065549 | 0.024642 | 5.174% | 11.52% | 21.85% | 53.6%
| N6 - L33 | 21.77 | 0 | 1.884 | 0 | 0 | 5.988 | 2.4 | 0 | 0.055444 | 3.425% | 5.711% | 13.86% | 20.33% | 2.2 | 0 | 0.049488 | 3.057% | 5.914% | 13.5% | 26.7% | 1.8 | 0 | 0.036963 | 2.283% | 6.691% | 12.32% | 51.6%
| N6 - L34 | 18.009 | 0 | 1.147 | 3.09 | 10.619 | 0.467 | 2.4 | 0.098324 | 0.0043241 | 5.992% | 9.982% | 24.58% | 20.73% | 2.2 | 0.08776 | 0.0038595 | 5.348% | 10.3% | 23.93% | 27.24% | 1.8 | 0.065549 | 0.0028827 | 3.994% | 11.52% | 21.85% | 52.7%
| N6 - L35 | 17.569 | 0 | 5.377 | 0.132 | 0.395 | 9.151 | 2.4 | 0.0036574 | 0.084731 | 9.778% | 10.17% | 21.18% | 20.41% | 2.2 | 0.0032645 | 0.075628 | 8.727% | 10.92% | 20.63% | 26.84% | 1.8 | 0.0024383 | 0.056488 | 6.518% | 13.65% | 18.83% | 52.01%
| N6 - L36 | 14.011 | 0 | 2.437 | 3.357 | 13.153 | 3.842 | 2.4 | 0.12179 | 0.035574 | 7.541% | 12.09% | 30.45% | 21.21% | 2.2 | 0.1087 | 0.031752 | 6.731% | 12.4% | 29.65% | 27.91% | 1.8 | 0.081191 | 0.023716 | 5.027% | 13.63% | 27.06% | 54.06%
| N6 - L37 | 19.506 | 0 | 5.648 | 0.266 | 0.805 | 8.954 | 2.4 | 0.0074537 | 0.082907 | 10.28% | 10.18% | 20.73% | 20.68% | 2.2 | 0.0066529 | 0.074 | 9.174% | 10.97% | 20.18% | 27.17% | 1.8 | 0.0049691 | 0.055272 | 6.852% | 13.89% | 18.42% | 52.51%
| N6 - L38 | 15.949 | 0 | 2.708 | 3.755 | 14.354 | 3.645 | 2.4 | 0.13291 | 0.03375 | 8.416% | 13.25% | 33.23% | 21.66% | 2.2 | 0.11863 | 0.030124 | 7.512% | 13.61% | 32.35% | 28.46% | 1.8 | 0.088605 | 0.0225 | 5.611% | 15% | 29.53% | 54.93%
| N6 - L39 | 21.159 | 0 | 1.925 | 1.263 | 9.786 | 5.747 | 2.4 | 0.090611 | 0.053213 | 4.185% | 8.282% | 22.65% | 21.87% | 2.2 | 0.080876 | 0.047496 | 3.736% | 8.301% | 22.06% | 28.67% | 1.8 | 0.060407 | 0.035475 | 2.79% | 8.444% | 20.14% | 55.08%
| N6 - L40 | 17.602 | 0 | 1.015 | 4.752 | 23.335 | 0.438 | 2.4 | 0.21606 | 0.0040556 | 8.833% | 20.76% | 54.02% | 23.14% | 2.2 | 0.19285 | 0.0036198 | 7.884% | 21.1% | 52.6% | 30.32% | 1.8 | 0.14404 | 0.0027037 | 5.889% | 22.52% | 48.01% | 58.06%
| N6 - L41 | 17.314 | 0 | 5.076 | 0.265 | 0.792 | 8.571 | 2.4 | 0.0073333 | 0.079361 | 9.24% | 9.551% | 19.84% | 20.34% | 2.2 | 0.0065455 | 0.070835 | 8.247% | 10.25% | 19.32% | 26.76% | 1.8 | 0.0048889 | 0.052907 | 6.16% | 12.84% | 17.64% | 51.88%
| N6 - L42 | 13.959 | 0 | 2.226 | 3.634 | 15.717 | 3.475 | 2.4 | 0.14553 | 0.032176 | 7.747% | 14.23% | 36.38% | 21.62% | 2.2 | 0.12989 | 0.028719 | 6.915% | 14.54% | 35.43% | 28.44% | 1.8 | 0.097019 | 0.021451 | 5.165% | 15.76% | 32.34% | 54.97%
| N6 - L43 | 19.058 | 0 | 5.32 | 0.532 | 1.612 | 8.394 | 2.4 | 0.014926 | 0.077722 | 9.719% | 9.556% | 19.43% | 20.66% | 2.2 | 0.013322 | 0.069372 | 8.675% | 10.3% | 18.92% | 27.15% | 1.8 | 0.0099506 | 0.051815 | 6.479% | 13.05% | 17.27% | 52.49%
| N6 - L44 | 15.703 | 0 | 2.47 | 4.431 | 18.122 | 3.298 | 2.4 | 0.1678 | 0.030537 | 9.222% | 16.55% | 41.95% | 22.3% | 2.2 | 0.14977 | 0.027256 | 8.231% | 16.94% | 40.85% | 29.28% | 1.8 | 0.11186 | 0.020358 | 6.148% | 18.51% | 37.29% | 56.35%
| N6 - L45 | 20.547 | 0 | 1.968 | 2.536 | 19.613 | 5.506 | 2.4 | 0.1816 | 0.050981 | 5.835% | 16.6% | 45.4% | 23.69% | 2.2 | 0.16209 | 0.045504 | 5.208% | 16.64% | 44.21% | 30.99% | 1.8 | 0.12107 | 0.033988 | 3.89% | 16.93% | 40.36% | 59.11%
| N6 - L46 | 17.192 | 0 | 0.882 | 6.435 | 36.123 | 0.41 | 2.4 | 0.33447 | 0.0037963 | 11.81% | 31.6% | 83.62% | 26.24% | 2.2 | 0.29854 | 0.0033884 | 10.54% | 31.97% | 81.42% | 34.24% | 1.8 | 0.22298 | 0.0025309 | 7.872% | 33.6% | 74.33% | 64.71%
| N6 - L47 | 17.314 | 0 | 5.076 | 0 | 0 | 8.571 | 2.4 | 0 | 0.079361 | 9.227% | 9.551% | 19.84% | 20.22% | 2.2 | 0 | 0.070835 | 8.236% | 10.25% | 19.32% | 26.6% | 1.8 | 0 | 0.052907 | 6.152% | 12.84% | 17.64% | 51.6%
| N6 - L48 | 13.959 | 0 | 2.226 | 3.899 | 16.51 | 3.475 | 2.4 | 0.15287 | 0.032176 | 8.162% | 15% | 38.22% | 21.77% | 2.2 | 0.13645 | 0.028719 | 7.285% | 15.33% | 37.21% | 28.63% | 1.8 | 0.10191 | 0.021451 | 5.441% | 16.67% | 33.97% | 55.3%
| N6 - L49 | 19.058 | 0 | 5.32 | 0 | 0 | 8.394 | 2.4 | 0 | 0.077722 | 9.671% | 9.556% | 19.43% | 20.4% | 2.2 | 0 | 0.069372 | 8.632% | 10.3% | 18.92% | 26.82% | 1.8 | 0 | 0.051815 | 6.447% | 13.05% | 17.27% | 51.91%
| N6 - L50 | 15.703 | 0 | 2.47 | 3.899 | 16.51 | 3.297 | 2.4 | 0.15287 | 0.030528 | 8.39% | 15% | 38.22% | 21.98% | 2.2 | 0.13645 | 0.027248 | 7.489% | 15.33% | 37.21% | 28.87% | 1.8 | 0.10191 | 0.020352 | 5.594% | 16.67% | 33.97% | 55.65%
| N6 - L51 | 20.547 | 0 | 1.968 | 0 | 0 | 5.506 | 2.4 | 0 | 0.050981 | 3.578% | 5.387% | 12.75% | 20.11% | 2.2 | 0 | 0.045504 | 3.193% | 5.615% | 12.41% | 26.42% | 1.8 | 0 | 0.033988 | 2.385% | 6.476% | 11.33% | 51.16%
| N6 - L52 | 17.192 | 0 | 0.882 | 3.899 | 16.51 | 0.41 | 2.4 | 0.15287 | 0.0037963 | 7.267% | 15% | 38.22% | 21.69% | 2.2 | 0.13645 | 0.0033884 | 6.486% | 15.33% | 37.21% | 28.48% | 1.8 | 0.10191 | 0.0025309 | 4.845% | 16.67% | 33.97% | 54.89%
| N6 - L53 | 26.788 | 0 | 5.244 | 0 | 0 | 9.102 | 2.4 | 0 | 0.084278 | 9.533% | 10.06% | 21.07% | 21.48% | 2.2 | 0 | 0.075223 | 8.509% | 10.78% | 20.52% | 28.11% | 1.8 | 0 | 0.056185 | 6.355% | 13.44% | 18.73% | 53.88%
| N6 - L54 | 20.536 | 0 | 0.484 | 5.95 | 25.983 | 0.254 | 2.4 | 0.24058 | 0.0023519 | 10.85% | 23.49% | 60.15% | 24.13% | 2.2 | 0.21474 | 0.0020992 | 9.686% | 23.99% | 58.56% | 31.53% | 1.8 | 0.16039 | 0.0015679 | 7.235% | 25.98% | 53.46% | 60%
| N6 - L55 | 21.629 | 0 | 4.683 | 0.019 | 2.341 | 8.499 | 2.4 | 0.021676 | 0.078694 | 8.513% | 9.268% | 19.67% | 21.12% | 2.2 | 0.019347 | 0.07024 | 7.598% | 9.904% | 19.16% | 27.7% | 1.8 | 0.014451 | 0.052463 | 5.675% | 12.25% | 17.49% | 53.37%
| N6 - L56 | 17.331 | 0 | 1.22 | 4.436 | 21.209 | 2.189 | 2.4 | 0.19638 | 0.020269 | 8.363% | 18.93% | 49.09% | 22.96% | 2.2 | 0.17528 | 0.018091 | 7.465% | 19.27% | 47.8% | 30.1% | 1.8 | 0.13092 | 0.013512 | 5.576% | 20.63% | 43.64% | 57.7%
400kV 3 Phase Pantograph Disconnector x 2400mm high | MAX | 25.83 |  | 8.94 | 9.66 | 57.24 | 41.44 | 2.7 |  | Worst Load Case = | 13.87% | 34.95% | 93.06% | 28.07% | 2.5 |  | Worst Load Case = | 12.14% | 34.25% | 87.92% | 36.08% | 2 |  | Worst Load Case = | 9.483% | 38.28% | 85.86% | 70.25%
| 1 | 16.54 | 0 | 0 | 9.2 | 54.51 | 0 | 2.7 | 0.39879 | 0 | 13.21% | 33.28% | 88.62% | 26.1% | 2.5 | 0.34886 | 0 | 11.56% | 32.62% | 83.73% | 33.66% | 2 | 0.27255 | 0 | 9.031% | 36.45% | 81.77% | 65.65%
| 2 | 16.54 | 0 | 5.44 | 4.65 | 32.49 | 24.16 | 2.7 | 0.2377 | 0.17675 | 10.28% | 19.5% | 52.82% | 25.68% | 2.5 | 0.20794 | 0.15462 | 8.992% | 19.02% | 49.9% | 33.21% | 2 | 0.16245 | 0.1208 | 7.025% | 20.9% | 48.74% | 64.85%
| 3 | 18.45 | 0 | 0 | 5.37 | 28.85 | 0 | 2.7 | 0.21107 | 0 | 7.713% | 17.82% | 46.9% | 22% | 2.5 | 0.18464 | 0 | 6.747% | 17.52% | 44.31% | 28.71% | 2 | 0.14425 | 0 | 5.271% | 19.8% | 43.28% | 56.18%
| 4 | 18.45 | 0 | 5.91 | 0 | 0 | 26.28 | 2.7 | 0 | 0.19226 | 8.489% | 16.64% | 42.73% | 21.64% | 2.5 | 0 | 0.16819 | 7.426% | 16.48% | 40.37% | 28.27% | 2 | 0 | 0.1314 | 5.802% | 19.05% | 39.42% | 55.35%
| 5 | 18.54 | 0 | 0.25 | 4.8 | 26.26 | 1.75 | 2.7 | 0.19212 | 0.012803 | 6.904% | 16.18% | 42.69% | 21.86% | 2.5 | 0.16806 | 0.0112 | 6.039% | 15.9% | 40.34% | 28.54% | 2 | 0.1313 | 0.00875 | 4.718% | 17.93% | 39.39% | 55.85%
| 6 | 18.54 | 0 | 5.69 | 0.25 | 4.25 | 25.9 | 2.7 | 0.031093 | 0.18948 | 8.181% | 16.35% | 42.11% | 22.11% | 2.5 | 0.0272 | 0.16576 | 7.156% | 16.17% | 39.78% | 28.85% | 2 | 0.02125 | 0.1295 | 5.591% | 18.64% | 38.85% | 56.44%
| 7 | 16.54 | 0 | 0.6 | 9.1 | 53.8 | 4.21 | 2.7 | 0.3936 | 0.0308 | 13.1% | 32.85% | 87.47% | 26.56% | 2.5 | 0.34432 | 0.026944 | 11.46% | 32.2% | 82.64% | 34.23% | 2 | 0.269 | 0.02105 | 8.952% | 36% | 80.7% | 66.74%
| 8 | 16.54 | 0 | 6.22 | 4.57 | 31.94 | 29.57 | 2.7 | 0.23367 | 0.21633 | 11.09% | 19.17% | 51.93% | 26.48% | 2.5 | 0.20442 | 0.18925 | 9.698% | 18.69% | 49.06% | 34.18% | 2 | 0.1597 | 0.14785 | 7.577% | 21% | 47.91% | 66.69%
| 9 | 18.45 | 0 | 0 | 5.34 | 28.63 | 0 | 2.7 | 0.20946 | 0 | 7.67% | 17.69% | 46.55% | 21.97% | 2.5 | 0.18323 | 0 | 6.71% | 17.39% | 43.98% | 28.67% | 2 | 0.14315 | 0 | 5.242% | 19.66% | 42.95% | 56.11%
| 10 | 18.45 | 0 | 6.15 | 0 | 0 | 27.94 | 2.7 | 0 | 0.20441 | 8.833% | 17.64% | 45.42% | 21.87% | 2.5 | 0 | 0.17882 | 7.727% | 17.45% | 42.92% | 28.55% | 2 | 0 | 0.1397 | 6.037% | 20.12% | 41.91% | 55.88%
| 11 | 18.54 | 0 | 0.25 | 4.79 | 26.18 | 1.75 | 2.7 | 0.19153 | 0.012803 | 6.889% | 16.13% | 42.56% | 21.85% | 2.5 | 0.16755 | 0.0112 | 6.027% | 15.86% | 40.21% | 28.52% | 2 | 0.1309 | 0.00875 | 4.708% | 17.88% | 39.27% | 55.82%
| 12 | 18.54 | 0 | 5.86 | 0.25 | 4.25 | 27.11 | 2.7 | 0.031093 | 0.19834 | 8.425% | 17.07% | 44.07% | 22.28% | 2.5 | 0.0272 | 0.1735 | 7.37% | 16.88% | 41.64% | 29.06% | 2 | 0.02125 | 0.13555 | 5.758% | 19.41% | 40.66% | 56.84%
| 13 | 16.54 | 0 | 1.2 | 9 | 53.09 | 8.41 | 2.7 | 0.3884 | 0.061527 | 13.04% | 32.43% | 86.31% | 27.05% | 2.5 | 0.33978 | 0.053824 | 11.41% | 31.79% | 81.55% | 34.82% | 2 | 0.26545 | 0.04205 | 8.913% | 35.55% | 79.64% | 67.87%
| 14 | 16.54 | 0 | 6.99 | 4.49 | 31.39 | 34.99 | 2.7 | 0.22965 | 0.25599 | 11.93% | 21.8% | 56.89% | 27.34% | 2.5 | 0.2009 | 0.22394 | 10.44% | 21.49% | 53.74% | 35.22% | 2 | 0.15695 | 0.17495 | 8.155% | 24.48% | 52.49% | 68.66%
| 15 | 18.45 | 0 | 0 | 5.31 | 28.42 | 0 | 2.7 | 0.20792 | 0 | 7.627% | 17.56% | 46.2% | 21.94% | 2.5 | 0.18189 | 0 | 6.672% | 17.27% | 43.65% | 28.63% | 2 | 0.1421 | 0 | 5.213% | 19.52% | 42.63% | 56.04%
| 16 | 18.45 | 0 | 6.38 | 0 | 0 | 29.6 | 2.7 | 0 | 0.21655 | 9.164% | 18.63% | 48.12% | 22.11% | 2.5 | 0 | 0.18944 | 8.016% | 18.42% | 45.47% | 28.84% | 2 | 0 | 0.148 | 6.263% | 21.18% | 44.4% | 56.43%
| 17 | 18.54 | 0 | 0.25 | 4.76 | 25.94 | 1.75 | 2.7 | 0.18978 | 0.012803 | 6.846% | 15.99% | 42.17% | 21.81% | 2.5 | 0.16602 | 0.0112 | 5.989% | 15.72% | 39.84% | 28.48% | 2 | 0.1297 | 0.00875 | 4.679% | 17.73% | 38.91% | 55.74%
| 18 | 18.54 | 0 | 6.04 | 0.25 | 4.25 | 28.33 | 2.7 | 0.031093 | 0.20726 | 8.683% | 17.81% | 46.06% | 22.46% | 2.5 | 0.0272 | 0.18131 | 7.596% | 17.6% | 43.51% | 29.27% | 2 | 0.02125 | 0.14165 | 5.934% | 20.2% | 42.49% | 57.24%
| 19 | 17.37 | 0 | 0 | 9.66 | 57.24 | 0 | 2.7 | 0.41877 | 0 | 13.87% | 34.95% | 93.06% | 26.77% | 2.5 | 0.36634 | 0 | 12.14% | 34.25% | 87.92% | 34.45% | 2 | 0.2862 | 0 | 9.483% | 38.28% | 85.86% | 67.1%
| 20 | 17.37 | 0 | 5.71 | 4.88 | 34.12 | 25.36 | 2.7 | 0.24962 | 0.18553 | 10.79% | 20.47% | 55.47% | 26.26% | 2.5 | 0.21837 | 0.1623 | 9.438% | 19.97% | 52.41% | 33.91% | 2 | 0.1706 | 0.1268 | 7.373% | 21.94% | 51.18% | 66.13%
| 21 | 25.83 | 0 | 0 | 7.52 | 40.39 | 0 | 2.7 | 0.29549 | 0 | 10.8% | 24.94% | 65.66% | 24.63% | 2.5 | 0.2585 | 0 | 9.449% | 24.53% | 62.04% | 31.84% | 2 | 0.20195 | 0 | 7.382% | 27.71% | 60.59% | 61.78%
| 22 | 25.83 | 0 | 8.27 | 0 | 0 | 36.79 | 2.7 | 0 | 0.26915 | 11.88% | 23.3% | 59.81% | 24.03% | 2.5 | 0 | 0.23546 | 10.39% | 23.07% | 56.51% | 31.12% | 2 | 0 | 0.18395 | 8.118% | 26.66% | 55.19% | 60.42%
| 23 | 22.25 | 0 | 0.3 | 5.76 | 31.52 | 2.1 | 2.7 | 0.2306 | 0.015364 | 8.284% | 19.42% | 51.24% | 23.07% | 2.5 | 0.20173 | 0.01344 | 7.247% | 19.09% | 48.41% | 29.98% | 2 | 0.1576 | 0.0105 | 5.662% | 21.52% | 47.28% | 58.43%
| 24 | 22.25 | 0 | 6.83 | 0.3 | 5.1 | 31.08 | 2.7 | 0.037311 | 0.22738 | 9.82% | 19.62% | 50.53% | 23.39% | 2.5 | 0.03264 | 0.19891 | 8.59% | 19.41% | 47.74% | 30.37% | 2 | 0.0255 | 0.1554 | 6.711% | 22.37% | 46.62% | 59.18%
| 25 | 17.37 | 0 | 0.63 | 9.56 | 56.49 | 4.42 | 2.7 | 0.41328 | 0.032337 | 13.76% | 34.5% | 91.84% | 27.26% | 2.5 | 0.36154 | 0.028288 | 12.04% | 33.82% | 86.77% | 35.06% | 2 | 0.28245 | 0.0221 | 9.405% | 37.8% | 84.74% | 68.26%
| 26 | 17.37 | 0 | 6.53 | 4.8 | 33.54 | 31.05 | 2.7 | 0.24538 | 0.22716 | 11.64% | 20.13% | 54.53% | 27.13% | 2.5 | 0.21466 | 0.19872 | 10.18% | 19.63% | 51.52% | 34.96% | 2 | 0.1677 | 0.15525 | 7.956% | 22.05% | 50.31% | 68.12%
| 27 | 25.83 | 0 | 0 | 7.47 | 40.09 | 0 | 2.7 | 0.2933 | 0 | 10.73% | 24.76% | 65.18% | 24.58% | 2.5 | 0.25658 | 0 | 9.386% | 24.35% | 61.58% | 31.78% | 2 | 0.20045 | 0 | 7.333% | 27.52% | 60.14% | 61.67%
| 28 | 25.83 | 0 | 8.6 | 0 | 0 | 39.12 | 2.7 | 0 | 0.2862 | 12.35% | 24.7% | 63.6% | 24.41% | 2.5 | 0 | 0.25037 | 10.81% | 24.43% | 60.09% | 31.58% | 2 | 0 | 0.1956 | 8.442% | 28.16% | 58.68% | 61.29%
| 29 | 22.25 | 0 | 0.3 | 5.75 | 31.41 | 2.1 | 2.7 | 0.22979 | 0.015364 | 8.27% | 19.36% | 51.07% | 23.05% | 2.5 | 0.20102 | 0.01344 | 7.235% | 19.03% | 48.25% | 29.96% | 2 | 0.15705 | 0.0105 | 5.652% | 21.45% | 47.12% | 58.4%
| 30 | 22.25 | 0 | 7.04 | 0.3 | 5.1 | 32.54 | 2.7 | 0.037311 | 0.23806 | 10.12% | 20.5% | 52.9% | 23.61% | 2.5 | 0.03264 | 0.20826 | 8.854% | 20.26% | 49.98% | 30.65% | 2 | 0.0255 | 0.1627 | 6.917% | 23.31% | 48.81% | 59.7%
| 31 | 17.37 | 0 | 1.26 | 9.45 | 55.74 | 8.83 | 2.7 | 0.40779 | 0.0646 | 13.69% | 34.05% | 90.62% | 27.78% | 2.5 | 0.35674 | 0.056512 | 11.98% | 33.38% | 85.62% | 35.69% | 2 | 0.2787 | 0.04415 | 9.359% | 37.32% | 83.61% | 69.47%
| 32 | 17.37 | 0 | 7.34 | 4.72 | 32.96 | 36.74 | 2.7 | 0.24113 | 0.26879 | 12.53% | 22.89% | 59.73% | 28.07% | 2.5 | 0.21094 | 0.23514 | 10.97% | 22.57% | 56.43% | 36.08% | 2 | 0.1648 | 0.1837 | 8.566% | 25.71% | 55.11% | 70.25%
| 33 | 25.83 | 0 | 0 | 7.43 | 39.78 | 0 | 2.7 | 0.29103 | 0 | 10.67% | 24.58% | 64.67% | 24.52% | 2.5 | 0.25459 | 0 | 9.336% | 24.17% | 61.1% | 31.71% | 2 | 0.1989 | 0 | 7.294% | 27.32% | 59.67% | 61.55%
| 34 | 25.83 | 0 | 8.94 | 0 | 0 | 41.44 | 2.7 | 0 | 0.30317 | 12.84% | 26.09% | 67.37% | 24.81% | 2.5 | 0 | 0.26522 | 11.23% | 25.79% | 63.65% | 32.06% | 2 | 0 | 0.2072 | 8.776% | 29.66% | 62.16% | 62.19%
| 35 | 22.25 | 0 | 0.3 | 5.71 | 31.13 | 2.1 | 2.7 | 0.22775 | 0.015364 | 8.213% | 19.19% | 50.61% | 23.01% | 2.5 | 0.19923 | 0.01344 | 7.185% | 18.86% | 47.82% | 29.91% | 2 | 0.15565 | 0.0105 | 5.613% | 21.27% | 46.7% | 58.3%
| 36 | 22.25 | 0 | 7.24 | 0.3 | 5.1 | 33.99 | 2.7 | 0.037311 | 0.24867 | 10.41% | 21.36% | 55.26% | 23.84% | 2.5 | 0.03264 | 0.21754 | 9.105% | 21.11% | 52.21% | 30.92% | 2 | 0.0255 | 0.16995 | 7.113% | 24.23% | 50.99% | 60.22%
400kV Disconnector with 2 Earth Switch Structure x 2500mm high | MAX | 31.124 |  | 12.046 | 7.352 | 20.494 | 20.265 | 1.8 |  | Worst Load Case = | 30% | 39.85% | 112.4% | 34.66% | 1.8 |  | Worst Load Case = | 29.21% | 44.32% | 84.34% | 37.94% | 1.4 |  | Worst Load Case = | 24.14% | 64.66% | 89.62% | 75.61%
| N7 - L1 | 9.164 | 0 | 0.69 | 0.392 | 0.269 | 8.97 | 1.8 | 0.004428 | 0.14765 | 2.228% | 15.08% | 49.22% | 22.55% | 1.8 | 0.003321 | 0.11074 | 1.923% | 13.25% | 36.91% | 27.91% | 1.4 | 0.0027449 | 0.091531 | 1.59% | 15.09% | 39.23% | 55.57%
| N7 - L2 | 10.49 | 0 | 3.257 | 3.368 | 9.029 | 0.961 | 1.8 | 0.14863 | 0.015819 | 12.91% | 18.02% | 49.54% | 23.21% | 1.8 | 0.11147 | 0.011864 | 11.36% | 17.01% | 37.16% | 28.52% | 1.4 | 0.092133 | 0.0098061 | 9.386% | 22.98% | 39.49% | 56.72%
| N7 - L3 | 9.441 | 0 | 5.708 | 0.372 | 0.233 | 12.731 | 1.8 | 0.0038354 | 0.20956 | 16% | 26.93% | 69.85% | 24.63% | 1.8 | 0.0028765 | 0.15717 | 13.86% | 25.29% | 52.39% | 29.71% | 1.4 | 0.0023776 | 0.12991 | 11.46% | 35.2% | 55.67% | 59.4%
| N7 - L4 | 10.767 | 0 | 1.761 | 3.388 | 9.065 | 2.799 | 1.8 | 0.14922 | 0.046074 | 10.48% | 18.03% | 49.74% | 24.12% | 1.8 | 0.11191 | 0.034556 | 9.255% | 17.08% | 37.3% | 29.35% | 1.4 | 0.0925 | 0.028561 | 7.649% | 23.09% | 39.64% | 58.46%
| N7 - L5 | 9.895 | 0 | 5.612 | 0.352 | 0.224 | 13.117 | 1.8 | 0.0036872 | 0.21592 | 15.63% | 27.25% | 71.97% | 24.98% | 1.8 | 0.0027654 | 0.16194 | 13.63% | 25.69% | 53.98% | 30.01% | 1.4 | 0.0022857 | 0.13385 | 11.26% | 35.48% | 57.36% | 60%
| N7 - L6 | 11.221 | 0 | 1.665 | 3.408 | 9.074 | 3.185 | 1.8 | 0.14937 | 0.052428 | 10.35% | 17.95% | 49.79% | 24.42% | 1.8 | 0.11202 | 0.039321 | 9.193% | 17.12% | 37.34% | 29.63% | 1.4 | 0.092592 | 0.0325 | 7.599% | 23.16% | 39.68% | 59%
| N7 - L7 | 8.927 | 0 | 0.785 | 0.82 | 0.641 | 8.938 | 1.8 | 0.010551 | 0.14713 | 3.199% | 15.19% | 49.04% | 22.63% | 1.8 | 0.0079136 | 0.11035 | 2.751% | 13.34% | 36.78% | 27.98% | 1.4 | 0.0065408 | 0.091204 | 2.274% | 15.32% | 39.09% | 55.75%
| N7 - L8 | 10.133 | 0 | 3.155 | 2.814 | 10.202 | 0.938 | 1.8 | 0.16793 | 0.01544 | 11.71% | 19.3% | 55.98% | 23.72% | 1.8 | 0.12595 | 0.01158 | 10.25% | 17.85% | 41.98% | 28.96% | 1.4 | 0.1041 | 0.0095714 | 8.469% | 23.08% | 44.62% | 57.7%
| N7 - L9 | 9.512 | 0 | 5.627 | 0.363 | 0.218 | 12.557 | 1.8 | 0.0035885 | 0.2067 | 15.76% | 26.53% | 68.9% | 24.54% | 1.8 | 0.0026914 | 0.15502 | 13.67% | 24.94% | 51.67% | 29.64% | 1.4 | 0.0022245 | 0.12813 | 11.3% | 34.71% | 54.91% | 59.23%
| N7 - L10 | 10.718 | 0 | 1.687 | 3.271 | 9.343 | 2.682 | 1.8 | 0.15379 | 0.044148 | 10.11% | 18.34% | 51.26% | 24.2% | 1.8 | 0.11535 | 0.033111 | 8.921% | 17.3% | 38.45% | 29.42% | 1.4 | 0.095337 | 0.027367 | 7.373% | 23.16% | 40.86% | 58.61%
| N7 - L11 | 9.946 | 0 | 5.545 | 0.35 | 0.225 | 12.952 | 1.8 | 0.0037037 | 0.2132 | 15.43% | 26.89% | 71.07% | 24.9% | 1.8 | 0.0027778 | 0.1599 | 13.47% | 25.37% | 53.3% | 29.94% | 1.4 | 0.0022959 | 0.13216 | 11.13% | 35.05% | 56.64% | 59.84%
| N7 - L12 | 11.152 | 0 | 1.605 | 3.284 | 9.336 | 3.077 | 1.8 | 0.15368 | 0.05065 | 9.981% | 18.23% | 51.23% | 24.5% | 1.8 | 0.11526 | 0.037988 | 8.86% | 17.31% | 38.42% | 29.69% | 1.4 | 0.095265 | 0.031398 | 7.323% | 23.18% | 40.83% | 59.13%
| N7 - L13 | 8.614 | 0 | 0.779 | 0.201 | 2.753 | 8.933 | 1.8 | 0.045317 | 0.14705 | 2.277% | 15.25% | 49.02% | 23.47% | 1.8 | 0.033988 | 0.11028 | 1.95% | 13.32% | 36.76% | 28.75% | 1.4 | 0.028092 | 0.091153 | 1.612% | 15.29% | 39.07% | 57.41%
| N7 - L14 | 9.728 | 0 | 3.159 | 4.129 | 12.923 | 0.939 | 1.8 | 0.21272 | 0.015457 | 14.48% | 25.26% | 70.91% | 25.15% | 1.8 | 0.15954 | 0.011593 | 12.6% | 23.39% | 53.18% | 30.17% | 1.4 | 0.13187 | 0.0095816 | 10.42% | 30.88% | 56.51% | 60.35%
| N7 - L15 | 9.505 | 0 | 5.631 | 0.355 | 0.2 | 12.556 | 1.8 | 0.0032922 | 0.20668 | 15.77% | 26.54% | 68.89% | 24.53% | 1.8 | 0.0024691 | 0.15501 | 13.68% | 24.95% | 51.67% | 29.63% | 1.4 | 0.0020408 | 0.12812 | 11.3% | 34.72% | 54.91% | 59.21%
| N7 - L16 | 10.619 | 0 | 1.693 | 3.573 | 9.97 | 2.685 | 1.8 | 0.16412 | 0.044198 | 10.88% | 19.69% | 54.71% | 24.51% | 1.8 | 0.12309 | 0.033148 | 9.583% | 18.58% | 41.03% | 29.69% | 1.4 | 0.10173 | 0.027398 | 7.921% | 24.95% | 43.6% | 59.2%
| N7 - L17 | 9.945 | 0 | 5.551 | 0.352 | 0.229 | 12.963 | 1.8 | 0.0037695 | 0.21338 | 15.45% | 26.92% | 71.13% | 24.91% | 1.8 | 0.0028272 | 0.16004 | 13.48% | 25.4% | 53.35% | 29.95% | 1.4 | 0.0023367 | 0.13228 | 11.14% | 35.08% | 56.69% | 59.86%
| N7 - L18 | 11.059 | 0 | 1.613 | 3.576 | 9.942 | 3.092 | 1.8 | 0.16365 | 0.050897 | 10.73% | 19.53% | 54.55% | 24.81% | 1.8 | 0.12274 | 0.038173 | 9.508% | 18.54% | 40.91% | 29.96% | 1.4 | 0.10145 | 0.031551 | 7.859% | 24.92% | 43.48% | 59.72%
| N7 - L19 | 9.242 | 0 | 0.779 | 1.061 | 0.933 | 8.932 | 1.8 | 0.015358 | 0.14703 | 3.692% | 15.11% | 49.01% | 22.83% | 1.8 | 0.011519 | 0.11027 | 3.19% | 13.32% | 36.76% | 28.17% | 1.4 | 0.0095204 | 0.091143 | 2.637% | 15.29% | 39.06% | 56.11%
| N7 - L20 | 10.356 | 0 | 3.159 | 4.99 | 11.103 | 0.939 | 1.8 | 0.18277 | 0.015457 | 16.31% | 23.2% | 60.92% | 24.27% | 1.8 | 0.13707 | 0.011593 | 14.31% | 22.08% | 45.69% | 29.44% | 1.4 | 0.1133 | 0.0095816 | 11.83% | 30.73% | 48.56% | 58.7%
| N7 - L21 | 9.499 | 0 | 5.638 | 0.37 | 0.232 | 12.572 | 1.8 | 0.0038189 | 0.20695 | 15.79% | 26.57% | 68.98% | 24.56% | 1.8 | 0.0028642 | 0.15521 | 13.69% | 24.98% | 51.74% | 29.65% | 1.4 | 0.0023673 | 0.12829 | 11.32% | 34.76% | 54.98% | 59.25%
| N7 - L22 | 10.613 | 0 | 1.7 | 3.559 | 9.939 | 2.701 | 1.8 | 0.1636 | 0.044461 | 10.85% | 19.63% | 54.53% | 24.5% | 1.8 | 0.1227 | 0.033346 | 9.56% | 18.52% | 40.9% | 29.68% | 1.4 | 0.10142 | 0.027561 | 7.902% | 24.86% | 43.47% | 59.18%
| N7 - L23 | 9.947 | 0 | 5.54 | 0.35 | 0.223 | 12.942 | 1.8 | 0.0036708 | 0.21304 | 15.42% | 26.87% | 71.01% | 24.89% | 1.8 | 0.0027531 | 0.15978 | 13.45% | 25.35% | 53.26% | 29.94% | 1.4 | 0.0022755 | 0.13206 | 11.12% | 35.02% | 56.6% | 59.83%
| N7 - L24 | 11.061 | 0 | 1.602 | 3.579 | 9.947 | 3.071 | 1.8 | 0.16374 | 0.050551 | 10.72% | 19.54% | 54.58% | 24.8% | 1.8 | 0.1228 | 0.037914 | 9.504% | 18.55% | 40.93% | 29.95% | 1.4 | 0.1015 | 0.031337 | 7.856% | 24.93% | 43.5% | 59.7%
| N7 - L25 | 12.134 | 0 | 4.048 | 0.411 | 0.282 | 10.813 | 1.8 | 0.004642 | 0.17799 | 10.96% | 21.11% | 59.33% | 24.27% | 1.8 | 0.0034815 | 0.13349 | 9.862% | 20.39% | 44.5% | 29.46% | 1.4 | 0.0028776 | 0.11034 | 8.151% | 27.56% | 47.29% | 58.56%
| N7 - L26 | 13.581 | 0 | 0.348 | 3.919 | 10.937 | 0.452 | 1.8 | 0.18003 | 0.0074403 | 10.39% | 20.74% | 60.01% | 24.79% | 1.8 | 0.13502 | 0.0055802 | 9.536% | 20.38% | 45.01% | 29.94% | 1.4 | 0.1116 | 0.0046122 | 7.882% | 27.37% | 47.83% | 59.42%
| N7 - L27 | 9.195 | 0 | 4.044 | 0.665 | 4.958 | 10.413 | 1.8 | 0.081613 | 0.17141 | 11.5% | 21.36% | 57.14% | 25.49% | 1.8 | 0.06121 | 0.12856 | 9.934% | 19.83% | 42.85% | 30.53% | 1.4 | 0.050592 | 0.10626 | 8.21% | 26.97% | 45.54% | 61.16%
| N7 - L28 | 10.339 | 0 | 0.099 | 4.595 | 15.129 | 0.485 | 1.8 | 0.24904 | 0.0079835 | 12.69% | 29.03% | 83.01% | 26.51% | 1.8 | 0.18678 | 0.0059877 | 11.14% | 27.06% | 62.26% | 31.28% | 1.4 | 0.15438 | 0.004949 | 9.208% | 35.45% | 66.16% | 62.69%
| N7 - L29 | 9.622 | 0 | 0.725 | 0.411 | 0.282 | 9.419 | 1.8 | 0.004642 | 0.15505 | 2.325% | 15.73% | 51.68% | 22.9% | 1.8 | 0.0034815 | 0.11628 | 2.02% | 13.91% | 38.76% | 28.22% | 1.4 | 0.0028776 | 0.096112 | 1.67% | 15.84% | 41.19% | 56.19%
| N7 - L30 | 11.014 | 0 | 3.42 | 3.536 | 9.481 | 1.009 | 1.8 | 0.15607 | 0.016609 | 13.46% | 18.79% | 52.02% | 23.59% | 1.8 | 0.11705 | 0.012457 | 11.92% | 17.86% | 39.02% | 28.87% | 1.4 | 0.096745 | 0.010296 | 9.855% | 24.13% | 41.46% | 57.41%
| N7 - L31 | 9.913 | 0 | 5.994 | 0.391 | 0.245 | 13.367 | 1.8 | 0.0040329 | 0.22003 | 16.69% | 28.09% | 73.34% | 25.15% | 1.8 | 0.0030247 | 0.16502 | 14.56% | 26.56% | 55.01% | 30.15% | 1.4 | 0.0025 | 0.1364 | 12.03% | 36.96% | 58.46% | 60.29%
| N7 - L32 | 11.306 | 0 | 1.849 | 3.557 | 9.518 | 2.939 | 1.8 | 0.15667 | 0.048379 | 10.92% | 18.79% | 52.22% | 24.57% | 1.8 | 0.11751 | 0.036284 | 9.717% | 17.94% | 39.17% | 29.75% | 1.4 | 0.097122 | 0.02999 | 8.031% | 24.24% | 41.62% | 59.25%
| N7 - L33 | 10.39 | 0 | 5.893 | 0.369 | 0.235 | 13.773 | 1.8 | 0.0038683 | 0.22672 | 16.3% | 28.41% | 75.57% | 25.52% | 1.8 | 0.0029012 | 0.17004 | 14.31% | 26.98% | 56.68% | 30.48% | 1.4 | 0.002398 | 0.14054 | 11.83% | 37.26% | 60.23% | 60.93%
| N7 - L34 | 11.782 | 0 | 1.748 | 3.578 | 9.528 | 3.344 | 1.8 | 0.15684 | 0.055045 | 10.78% | 18.71% | 52.28% | 24.89% | 1.8 | 0.11763 | 0.041284 | 9.652% | 17.98% | 39.21% | 30.05% | 1.4 | 0.097224 | 0.034122 | 7.978% | 24.32% | 41.67% | 59.83%
| N7 - L35 | 9.373 | 0 | 0.824 | 0.861 | 0.673 | 9.384 | 1.8 | 0.011078 | 0.15447 | 3.337% | 15.85% | 51.49% | 22.98% | 1.8 | 0.0083086 | 0.11585 | 2.889% | 14% | 38.62% | 28.3% | 1.4 | 0.0068673 | 0.095755 | 2.388% | 16.08% | 41.04% | 56.38%
| N7 - L36 | 10.639 | 0 | 3.313 | 2.955 | 10.712 | 0.985 | 1.8 | 0.17633 | 0.016214 | 12.21% | 20.12% | 58.78% | 24.14% | 1.8 | 0.13225 | 0.01216 | 10.76% | 18.75% | 44.08% | 29.34% | 1.4 | 0.10931 | 0.010051 | 8.894% | 24.23% | 46.85% | 58.45%
| N7 - L37 | 9.988 | 0 | 5.908 | 0.381 | 0.229 | 13.185 | 1.8 | 0.0037695 | 0.21704 | 16.43% | 27.67% | 72.35% | 25.05% | 1.8 | 0.0028272 | 0.16278 | 14.35% | 26.19% | 54.26% | 30.07% | 1.4 | 0.0023367 | 0.13454 | 11.86% | 36.44% | 57.66% | 60.11%
| N7 - L38 | 11.254 | 0 | 1.771 | 3.435 | 9.81 | 2.816 | 1.8 | 0.16148 | 0.046354 | 10.54% | 19.11% | 53.83% | 24.66% | 1.8 | 0.12111 | 0.034765 | 9.367% | 18.17% | 40.37% | 29.83% | 1.4 | 0.1001 | 0.028735 | 7.742% | 24.31% | 42.9% | 59.41%
| N7 - L39 | 10.443 | 0 | 5.823 | 0.368 | 0.236 | 13.6 | 1.8 | 0.0038848 | 0.22387 | 16.09% | 28.04% | 74.62% | 25.43% | 1.8 | 0.0029136 | 0.1679 | 14.14% | 26.64% | 55.97% | 30.4% | 1.4 | 0.0024082 | 0.13878 | 11.69% | 36.8% | 59.48% | 60.77%
| N7 - L40 | 11.71 | 0 | 1.686 | 3.448 | 9.803 | 3.231 | 1.8 | 0.16137 | 0.053185 | 10.4% | 19% | 53.79% | 24.97% | 1.8 | 0.12102 | 0.039889 | 9.303% | 18.18% | 40.34% | 30.11% | 1.4 | 0.10003 | 0.032969 | 7.689% | 24.34% | 42.87% | 59.97%
| N7 - L41 | 9.045 | 0 | 0.818 | 0.211 | 2.89 | 9.379 | 1.8 | 0.047572 | 0.15439 | 2.376% | 15.91% | 51.46% | 23.88% | 1.8 | 0.035679 | 0.11579 | 2.048% | 13.99% | 38.6% | 29.11% | 1.4 | 0.02949 | 0.095704 | 1.692% | 16.06% | 41.02% | 58.14%
| N7 - L42 | 10.215 | 0 | 3.317 | 4.336 | 13.569 | 0.986 | 1.8 | 0.22336 | 0.01623 | 15.1% | 26.34% | 74.45% | 25.7% | 1.8 | 0.16752 | 0.012173 | 13.23% | 24.56% | 55.84% | 30.64% | 1.4 | 0.13846 | 0.010061 | 10.94% | 32.42% | 59.34% | 61.31%
| N7 - L43 | 9.98 | 0 | 5.912 | 0.373 | 0.21 | 13.184 | 1.8 | 0.0034568 | 0.21702 | 16.44% | 27.68% | 72.34% | 25.04% | 1.8 | 0.0025926 | 0.16277 | 14.36% | 26.19% | 54.26% | 30.06% | 1.4 | 0.0021429 | 0.13453 | 11.87% | 36.45% | 57.66% | 60.09%
| N7 - L44 | 11.15 | 0 | 1.777 | 3.752 | 10.468 | 2.819 | 1.8 | 0.17231 | 0.046403 | 11.34% | 20.53% | 57.44% | 25% | 1.8 | 0.12923 | 0.034802 | 10.06% | 19.51% | 43.08% | 30.12% | 1.4 | 0.10682 | 0.028765 | 8.317% | 26.2% | 45.78% | 60.05%
| N7 - L45 | 10.443 | 0 | 5.828 | 0.37 | 0.24 | 13.611 | 1.8 | 0.0039506 | 0.22405 | 16.1% | 28.06% | 74.68% | 25.44% | 1.8 | 0.002963 | 0.16804 | 14.15% | 26.67% | 56.01% | 30.41% | 1.4 | 0.002449 | 0.13889 | 11.7% | 36.83% | 59.52% | 60.78%
| N7 - L46 | 11.612 | 0 | 1.693 | 3.755 | 10.439 | 3.246 | 1.8 | 0.17184 | 0.053432 | 11.18% | 20.35% | 57.28% | 25.31% | 1.8 | 0.12888 | 0.040074 | 9.984% | 19.47% | 42.96% | 30.4% | 1.4 | 0.10652 | 0.033122 | 8.252% | 26.16% | 45.65% | 60.6%
| N7 - L47 | 9.704 | 0 | 0.818 | 1.114 | 0.98 | 9.379 | 1.8 | 0.016132 | 0.15439 | 3.851% | 15.76% | 51.46% | 23.2% | 1.8 | 0.012099 | 0.11579 | 3.35% | 13.99% | 38.6% | 28.5% | 1.4 | 0.01 | 0.095704 | 2.769% | 16.06% | 41.02% | 56.76%
| N7 - L48 | 10.874 | 0 | 3.317 | 5.239 | 11.658 | 0.986 | 1.8 | 0.1919 | 0.01623 | 17% | 24.18% | 63.97% | 24.74% | 1.8 | 0.14393 | 0.012173 | 15.03% | 23.18% | 47.98% | 29.85% | 1.4 | 0.11896 | 0.010061 | 12.42% | 32.27% | 50.98% | 59.52%
| N7 - L49 | 9.974 | 0 | 5.92 | 0.388 | 0.243 | 13.201 | 1.8 | 0.004 | 0.2173 | 16.47% | 27.71% | 72.43% | 25.06% | 1.8 | 0.003 | 0.16298 | 14.38% | 26.23% | 54.33% | 30.08% | 1.4 | 0.0024796 | 0.1347 | 11.89% | 36.5% | 57.73% | 60.14%
| N7 - L50 | 11.144 | 0 | 1.785 | 3.737 | 10.435 | 2.836 | 1.8 | 0.17177 | 0.046683 | 11.31% | 20.46% | 57.26% | 24.99% | 1.8 | 0.12883 | 0.035012 | 10.04% | 19.44% | 42.94% | 30.11% | 1.4 | 0.10648 | 0.028939 | 8.297% | 26.11% | 45.63% | 60.03%
| N7 - L51 | 10.444 | 0 | 5.817 | 0.367 | 0.234 | 13.589 | 1.8 | 0.0038519 | 0.22369 | 16.07% | 28.02% | 74.56% | 25.42% | 1.8 | 0.0028889 | 0.16777 | 14.13% | 26.62% | 55.92% | 30.39% | 1.4 | 0.0023878 | 0.13866 | 11.68% | 36.77% | 59.43% | 60.75%
| N7 - L52 | 11.614 | 0 | 1.682 | 3.758 | 10.445 | 3.224 | 1.8 | 0.17193 | 0.05307 | 11.17% | 20.37% | 57.31% | 25.31% | 1.8 | 0.12895 | 0.039802 | 9.979% | 19.48% | 42.98% | 30.4% | 1.4 | 0.10658 | 0.032898 | 8.248% | 26.18% | 45.68% | 60.59%
| N7 - L53 | 16.987 | 0 | 5.667 | 0.575 | 0.395 | 15.139 | 1.8 | 0.0065021 | 0.2492 | 14.39% | 27.71% | 83.07% | 28.38% | 1.8 | 0.0048765 | 0.1869 | 13.81% | 28.54% | 62.3% | 32.99% | 1.4 | 0.0040306 | 0.15448 | 11.41% | 38.59% | 66.21% | 65.53%
| N7 - L54 | 19.013 | 0 | 0.487 | 5.486 | 15.311 | 0.633 | 1.8 | 0.25203 | 0.01042 | 13.56% | 27.06% | 84.01% | 29.21% | 1.8 | 0.18902 | 0.0078148 | 13.35% | 28.53% | 63.01% | 33.73% | 1.4 | 0.15623 | 0.0064592 | 11.03% | 38.31% | 66.96% | 66.87%
| N7 - L55 | 11.034 | 0 | 4.853 | 0.798 | 5.95 | 12.496 | 1.8 | 0.097942 | 0.2057 | 13.45% | 24.98% | 68.57% | 27.85% | 1.8 | 0.073457 | 0.15427 | 11.92% | 23.8% | 51.42% | 32.55% | 1.4 | 0.060714 | 0.12751 | 9.853% | 32.36% | 54.65% | 65.27%
| N7 - L56 | 12.407 | 0 | 0.118 | 5.513 | 18.155 | 0.583 | 1.8 | 0.29885 | 0.0095967 | 14.8% | 33.85% | 99.62% | 29.4% | 1.8 | 0.22414 | 0.0071975 | 13.37% | 32.47% | 74.71% | 33.63% | 1.4 | 0.18526 | 0.005949 | 11.05% | 42.54% | 79.4% | 67.51%
| N8 - L1 | 14.977 | 0 | 10.874 | 0.121 | 0.137 | 17.329 | 1.8 | 0.0022551 | 0.28525 | 28.19% | 37.39% | 95.08% | 29.29% | 1.8 | 0.0016914 | 0.21394 | 26.36% | 38.69% | 71.31% | 33.62% | 1.4 | 0.001398 | 0.17683 | 21.79% | 56.96% | 75.78% | 67.16%
| N8 - L2 | 12.981 | 0 | 3.248 | 4.274 | 10.753 | 4.569 | 1.8 | 0.177 | 0.07521 | 14.29% | 21.04% | 59% | 26.55% | 1.8 | 0.13275 | 0.056407 | 13.01% | 20.61% | 44.25% | 31.5% | 1.4 | 0.10972 | 0.046622 | 10.75% | 28.14% | 47.02% | 62.78%
| N8 - L3 | 14.169 | 0 | 5.624 | 0.154 | 0.136 | 12.521 | 1.8 | 0.0022387 | 0.20611 | 14.74% | 24.83% | 68.7% | 25.73% | 1.8 | 0.001679 | 0.15458 | 13.64% | 24.89% | 51.53% | 30.74% | 1.4 | 0.0013878 | 0.12777 | 11.27% | 34.65% | 54.76% | 61.06%
| N8 - L4 | 12.172 | 0 | 2.003 | 4.242 | 10.754 | 0.239 | 1.8 | 0.17702 | 0.0039342 | 12.63% | 21.23% | 59.01% | 24.23% | 1.8 | 0.13277 | 0.0029506 | 11.37% | 20.57% | 44.26% | 29.43% | 1.4 | 0.10973 | 0.0024388 | 9.398% | 28.04% | 47.03% | 58.48%
| N8 - L5 | 13.538 | 0 | 10.905 | 0.179 | 0.134 | 17.416 | 1.8 | 0.0022058 | 0.28668 | 28.82% | 38.28% | 95.56% | 28.92% | 1.8 | 0.0016543 | 0.21501 | 26.44% | 38.85% | 71.67% | 33.28% | 1.4 | 0.0013673 | 0.17771 | 21.85% | 57.18% | 76.16% | 66.61%
| N8 - L6 | 11.542 | 0 | 3.279 | 4.216 | 10.756 | 4.655 | 1.8 | 0.17705 | 0.076626 | 14.51% | 21.39% | 59.02% | 26.19% | 1.8 | 0.13279 | 0.057469 | 12.95% | 20.54% | 44.26% | 31.17% | 1.4 | 0.10976 | 0.0475 | 10.7% | 27.97% | 47.04% | 62.25%
| N8 - L7 | 14.95 | 0 | 10.716 | 0.113 | 0.117 | 17.082 | 1.8 | 0.0019259 | 0.28119 | 27.79% | 36.87% | 93.73% | 29.08% | 1.8 | 0.0014444 | 0.21089 | 25.98% | 38.13% | 70.3% | 33.46% | 1.4 | 0.0011939 | 0.17431 | 21.47% | 56.14% | 74.7% | 66.81%
| N8 - L8 | 12.855 | 0 | 3.136 | 4.157 | 11.036 | 4.413 | 1.8 | 0.18166 | 0.072642 | 13.89% | 21.37% | 60.55% | 26.6% | 1.8 | 0.13625 | 0.054481 | 12.62% | 20.84% | 45.42% | 31.54% | 1.4 | 0.11261 | 0.045031 | 10.43% | 28.21% | 48.26% | 62.88%
| N8 - L9 | 13.85 | 0 | 5.649 | 0.593 | 0.757 | 12.442 | 1.8 | 0.012461 | 0.20481 | 14.95% | 24.84% | 68.27% | 25.89% | 1.8 | 0.0093457 | 0.1536 | 13.77% | 24.82% | 51.2% | 30.89% | 1.4 | 0.0077245 | 0.12696 | 11.38% | 34.61% | 54.41% | 61.4%
| N8 - L10 | 11.755 | 0 | 1.931 | 3.677 | 11.911 | 0.226 | 1.8 | 0.19607 | 0.0037202 | 11.25% | 22.48% | 65.36% | 24.77% | 1.8 | 0.14705 | 0.0027901 | 10.07% | 21.38% | 49.02% | 29.88% | 1.4 | 0.12154 | 0.0023061 | 8.32% | 28.08% | 52.09% | 59.49%
| N8 - L11 | 13.552 | 0 | 10.773 | 0.174 | 0.123 | 17.201 | 1.8 | 0.0020247 | 0.28314 | 28.47% | 37.8% | 94.38% | 28.75% | 1.8 | 0.0015185 | 0.21236 | 26.12% | 38.37% | 70.79% | 33.15% | 1.4 | 0.0012551 | 0.17552 | 21.58% | 56.48% | 75.22% | 66.33%
| N8 - L12 | 11.458 | 0 | 3.194 | 4.097 | 11.03 | 4.532 | 1.8 | 0.18156 | 0.074601 | 14.12% | 21.7% | 60.52% | 26.27% | 1.8 | 0.13617 | 0.055951 | 12.59% | 20.75% | 45.39% | 31.23% | 1.4 | 0.11255 | 0.046245 | 10.41% | 28.02% | 48.24% | 62.39%
| N8 - L13 | 14.947 | 0 | 10.712 | 0.108 | 0.106 | 17.081 | 1.8 | 0.0017449 | 0.28117 | 27.78% | 36.86% | 93.72% | 29.07% | 1.8 | 0.0013086 | 0.21088 | 25.97% | 38.12% | 70.29% | 33.45% | 1.4 | 0.0010816 | 0.1743 | 21.46% | 56.13% | 74.7% | 66.79%
| N8 - L14 | 12.761 | 0 | 3.132 | 4.457 | 11.658 | 4.412 | 1.8 | 0.1919 | 0.072626 | 14.55% | 22.67% | 63.97% | 26.96% | 1.8 | 0.14393 | 0.054469 | 13.2% | 22.11% | 47.98% | 31.84% | 1.4 | 0.11896 | 0.04502 | 10.91% | 29.99% | 50.98% | 63.53%
| N8 - L15 | 13.55 | 0 | 5.648 | 0.418 | 2.847 | 12.441 | 1.8 | 0.046864 | 0.20479 | 14.96% | 24.94% | 68.26% | 26.85% | 1.8 | 0.035148 | 0.15359 | 13.73% | 24.81% | 51.2% | 31.73% | 1.4 | 0.029051 | 0.12695 | 11.35% | 34.6% | 54.41% | 63.22%
| N8 - L16 | 11.364 | 0 | 1.932 | 4.982 | 14.61 | 0.228 | 1.8 | 0.24049 | 0.0037531 | 14.55% | 28.27% | 80.16% | 26.33% | 1.8 | 0.18037 | 0.0028148 | 12.95% | 26.88% | 60.12% | 31.16% | 1.4 | 0.14908 | 0.0023265 | 10.7% | 35.82% | 63.89% | 62.3%
| N8 - L17 | 13.552 | 0 | 10.774 | 0.165 | 0.105 | 17.197 | 1.8 | 0.0017284 | 0.28308 | 28.47% | 37.8% | 94.36% | 28.74% | 1.8 | 0.0012963 | 0.21231 | 26.12% | 38.37% | 70.77% | 33.14% | 1.4 | 0.0010714 | 0.17548 | 21.59% | 56.48% | 75.21% | 66.31%
| N8 - L18 | 11.367 | 0 | 3.194 | 4.4 | 11.659 | 4.528 | 1.8 | 0.19192 | 0.074535 | 14.8% | 23.05% | 63.97% | 26.63% | 1.8 | 0.14394 | 0.055901 | 13.18% | 22.03% | 47.98% | 31.53% | 1.4 | 0.11897 | 0.046204 | 10.89% | 29.82% | 50.99% | 63.03%
| N8 - L19 | 14.953 | 0 | 10.722 | 0.122 | 0.137 | 17.09 | 1.8 | 0.0022551 | 0.28132 | 27.81% | 36.89% | 93.77% | 29.1% | 1.8 | 0.0016914 | 0.21099 | 25.99% | 38.15% | 70.33% | 33.47% | 1.4 | 0.001398 | 0.17439 | 21.48% | 56.17% | 74.74% | 66.84%
| N8 - L20 | 12.768 | 0 | 3.143 | 4.443 | 11.626 | 4.421 | 1.8 | 0.19137 | 0.072774 | 14.53% | 22.61% | 63.79% | 26.95% | 1.8 | 0.14353 | 0.05458 | 13.19% | 22.04% | 47.84% | 31.82% | 1.4 | 0.11863 | 0.045112 | 10.9% | 29.9% | 50.84% | 63.5%
| N8 - L21 | 14.194 | 0 | 5.648 | 1.296 | 1.06 | 12.441 | 1.8 | 0.017449 | 0.20479 | 15.18% | 24.73% | 68.26% | 26.13% | 1.8 | 0.013086 | 0.15359 | 14.05% | 24.81% | 51.2% | 31.1% | 1.4 | 0.010816 | 0.12695 | 11.61% | 34.6% | 54.41% | 61.82%
| N8 - L22 | 12.009 | 0 | 1.932 | 5.861 | 12.824 | 0.227 | 1.8 | 0.21109 | 0.0037366 | 16.65% | 26.3% | 70.36% | 25.38% | 1.8 | 0.15832 | 0.0028025 | 14.96% | 25.63% | 52.77% | 30.4% | 1.4 | 0.13086 | 0.0023163 | 12.36% | 35.78% | 56.08% | 60.57%
| N8 - L23 | 13.577 | 0 | 10.73 | 0.177 | 0.133 | 17.138 | 1.8 | 0.0021893 | 0.28211 | 28.35% | 37.65% | 94.04% | 28.72% | 1.8 | 0.001642 | 0.21158 | 26.01% | 38.23% | 70.53% | 33.13% | 1.4 | 0.0013571 | 0.17488 | 21.5% | 56.27% | 74.95% | 66.27%
| N8 - L24 | 11.392 | 0 | 3.15 | 4.388 | 11.63 | 4.469 | 1.8 | 0.19144 | 0.073564 | 14.7% | 22.98% | 63.81% | 26.58% | 1.8 | 0.14358 | 0.055173 | 13.09% | 21.97% | 47.86% | 31.49% | 1.4 | 0.11867 | 0.045602 | 10.82% | 29.75% | 50.86% | 62.95%
| N8 - L25 | 16.559 | 0 | 8.6 | 0.205 | 0.187 | 14.467 | 1.8 | 0.0030782 | 0.23814 | 21.85% | 30.06% | 79.38% | 27.67% | 1.8 | 0.0023086 | 0.1786 | 20.85% | 31.64% | 59.53% | 32.4% | 1.4 | 0.0019082 | 0.14762 | 17.23% | 46.16% | 63.27% | 64.34%
| N8 - L26 | 14.176 | 0 | 0.037 | 4.86 | 12.871 | 0.065 | 1.8 | 0.21187 | 0.00107 | 12.74% | 24.49% | 70.62% | 25.92% | 1.8 | 0.1589 | 0.00080247 | 11.78% | 24.32% | 52.97% | 30.89% | 1.4 | 0.13134 | 0.00066327 | 9.737% | 32.93% | 56.29% | 61.39%
| N8 - L27 | 13.209 | 0 | 8.244 | 0.85 | 5.047 | 13.794 | 1.8 | 0.083078 | 0.22706 | 22% | 30.01% | 75.69% | 28.87% | 1.8 | 0.062309 | 0.1703 | 20.09% | 30.23% | 56.77% | 33.42% | 1.4 | 0.0515 | 0.14076 | 16.6% | 44.14% | 60.32% | 66.87%
| N8 - L28 | 11.026 | 0 | 0.622 | 5.415 | 16.81 | 1.039 | 1.8 | 0.27671 | 0.017103 | 14.91% | 32.31% | 92.24% | 28.18% | 1.8 | 0.20753 | 0.012827 | 13.21% | 30.49% | 69.18% | 32.66% | 1.4 | 0.17153 | 0.010602 | 10.92% | 40.29% | 73.51% | 65.57%
| N8 - L29 | 15.726 | 0 | 11.418 | 0.127 | 0.144 | 18.196 | 1.8 | 0.0023704 | 0.29952 | 29.31% | 38.88% | 99.84% | 30.22% | 1.8 | 0.0017778 | 0.22464 | 27.68% | 40.62% | 74.88% | 34.36% | 1.4 | 0.0014694 | 0.18567 | 22.88% | 59.81% | 79.57% | 68.67%
| N8 - L30 | 13.63 | 0 | 3.41 | 4.488 | 11.291 | 4.797 | 1.8 | 0.18586 | 0.078963 | 14.88% | 21.9% | 61.95% | 27.19% | 1.8 | 0.1394 | 0.059222 | 13.66% | 21.64% | 46.47% | 32.05% | 1.4 | 0.11521 | 0.048949 | 11.29% | 29.54% | 49.38% | 63.88%
| N8 - L31 | 14.877 | 0 | 5.905 | 0.162 | 0.143 | 13.147 | 1.8 | 0.0023539 | 0.21641 | 15.34% | 25.82% | 72.14% | 26.32% | 1.8 | 0.0017654 | 0.16231 | 14.32% | 26.13% | 54.1% | 31.25% | 1.4 | 0.0014592 | 0.13415 | 11.83% | 36.38% | 57.49% | 62.06%
| N8 - L32 | 12.781 | 0 | 2.103 | 4.454 | 11.292 | 0.251 | 1.8 | 0.18588 | 0.0041317 | 13.15% | 22.11% | 61.96% | 24.7% | 1.8 | 0.13941 | 0.0030988 | 11.94% | 21.6% | 46.47% | 29.84% | 1.4 | 0.11522 | 0.0025612 | 9.868% | 29.45% | 49.38% | 59.29%
| N8 - L33 | 14.215 | 0 | 11.45 | 0.188 | 0.141 | 18.286 | 1.8 | 0.002321 | 0.301 | 29.99% | 39.83% | 100.3% | 29.83% | 1.8 | 0.0017407 | 0.22575 | 27.76% | 40.79% | 75.25% | 34% | 1.4 | 0.0014388 | 0.18659 | 22.94% | 60.04% | 79.97% | 68.09%
| N8 - L34 | 12.119 | 0 | 3.443 | 4.427 | 11.294 | 4.887 | 1.8 | 0.18591 | 0.080444 | 15.11% | 22.28% | 61.97% | 26.81% | 1.8 | 0.13943 | 0.060333 | 13.59% | 21.57% | 46.48% | 31.7% | 1.4 | 0.11524 | 0.049867 | 11.24% | 29.37% | 49.39% | 63.31%
| N8 - L35 | 15.698 | 0 | 11.251 | 0.119 | 0.123 | 17.936 | 1.8 | 0.0020247 | 0.29524 | 28.9% | 38.33% | 98.41% | 29.99% | 1.8 | 0.0015185 | 0.22143 | 27.27% | 40.04% | 73.81% | 34.18% | 1.4 | 0.0012551 | 0.18302 | 22.54% | 58.95% | 78.44% | 68.28%
| N8 - L36 | 13.498 | 0 | 3.293 | 4.365 | 11.588 | 4.634 | 1.8 | 0.19075 | 0.07628 | 14.46% | 22.24% | 63.58% | 27.25% | 1.8 | 0.14306 | 0.05721 | 13.25% | 21.88% | 47.69% | 32.09% | 1.4 | 0.11824 | 0.047286 | 10.95% | 29.62% | 50.68% | 63.99%
| N8 - L37 | 14.542 | 0 | 5.931 | 0.623 | 0.795 | 13.064 | 1.8 | 0.013086 | 0.21505 | 15.55% | 25.84% | 71.68% | 26.49% | 1.8 | 0.0098148 | 0.16128 | 14.45% | 26.06% | 53.76% | 31.4% | 1.4 | 0.0081122 | 0.13331 | 11.95% | 36.34% | 57.13% | 62.42%
| N8 - L38 | 12.343 | 0 | 2.027 | 3.861 | 12.506 | 0.237 | 1.8 | 0.20586 | 0.0039012 | 11.71% | 23.41% | 68.62% | 25.28% | 1.8 | 0.1544 | 0.0029259 | 10.57% | 22.45% | 51.47% | 30.32% | 1.4 | 0.12761 | 0.0024184 | 8.736% | 29.49% | 54.69% | 60.38%
| N8 - L39 | 14.23 | 0 | 11.312 | 0.182 | 0.13 | 18.061 | 1.8 | 0.0021399 | 0.2973 | 29.62% | 39.34% | 99.1% | 29.64% | 1.8 | 0.0016049 | 0.22298 | 27.42% | 40.29% | 74.33% | 33.86% | 1.4 | 0.0013265 | 0.1843 | 22.66% | 59.31% | 78.98% | 67.78%
| N8 - L40 | 12.031 | 0 | 3.354 | 4.301 | 11.581 | 4.759 | 1.8 | 0.19063 | 0.078337 | 14.71% | 22.6% | 63.54% | 26.89% | 1.8 | 0.14298 | 0.058753 | 13.22% | 21.79% | 47.66% | 31.77% | 1.4 | 0.11817 | 0.048561 | 10.93% | 29.42% | 50.65% | 63.47%
| N8 - L41 | 15.694 | 0 | 11.247 | 0.114 | 0.111 | 17.935 | 1.8 | 0.0018272 | 0.29523 | 28.89% | 38.33% | 98.41% | 29.98% | 1.8 | 0.0013704 | 0.22142 | 27.26% | 40.03% | 73.81% | 34.18% | 1.4 | 0.0011327 | 0.18301 | 22.53% | 58.93% | 78.43% | 68.27%
| N8 - L42 | 13.399 | 0 | 3.289 | 4.68 | 12.24 | 4.632 | 1.8 | 0.20148 | 0.076247 | 15.15% | 23.6% | 67.16% | 27.64% | 1.8 | 0.15111 | 0.057185 | 13.86% | 23.21% | 50.37% | 32.41% | 1.4 | 0.1249 | 0.047265 | 11.46% | 31.49% | 53.53% | 64.69%
| N8 - L43 | 14.227 | 0 | 5.93 | 0.438 | 2.989 | 13.063 | 1.8 | 0.049202 | 0.21503 | 15.57% | 25.95% | 71.68% | 27.52% | 1.8 | 0.036901 | 0.16127 | 14.41% | 26.05% | 53.76% | 32.3% | 1.4 | 0.0305 | 0.1333 | 11.91% | 36.33% | 57.13% | 64.37%
| N8 - L44 | 11.933 | 0 | 2.029 | 5.232 | 15.34 | 0.239 | 1.8 | 0.25251 | 0.0039342 | 15.16% | 29.45% | 84.17% | 26.99% | 1.8 | 0.18938 | 0.0029506 | 13.6% | 28.22% | 63.13% | 31.71% | 1.4 | 0.15653 | 0.0024388 | 11.24% | 37.62% | 67.08% | 63.41%
| N8 - L45 | 14.23 | 0 | 11.313 | 0.174 | 0.11 | 18.057 | 1.8 | 0.0018107 | 0.29723 | 29.63% | 39.33% | 99.08% | 29.63% | 1.8 | 0.001358 | 0.22293 | 27.42% | 40.29% | 74.31% | 33.85% | 1.4 | 0.0011224 | 0.18426 | 22.67% | 59.3% | 78.97% | 67.75%
| N8 - L46 | 11.935 | 0 | 3.354 | 4.62 | 12.241 | 4.755 | 1.8 | 0.2015 | 0.078272 | 15.42% | 24.01% | 67.17% | 27.28% | 1.8 | 0.15112 | 0.058704 | 13.84% | 23.13% | 50.37% | 32.08% | 1.4 | 0.12491 | 0.04852 | 11.44% | 31.31% | 53.53% | 64.16%
| N8 - L47 | 15.701 | 0 | 11.258 | 0.128 | 0.144 | 17.944 | 1.8 | 0.0023704 | 0.29537 | 28.91% | 38.35% | 98.46% | 30.01% | 1.8 | 0.0017778 | 0.22153 | 27.29% | 40.06% | 73.84% | 34.2% | 1.4 | 0.0014694 | 0.1831 | 22.56% | 58.98% | 78.47% | 68.32%
| N8 - L48 | 13.406 | 0 | 3.3 | 4.665 | 12.207 | 4.642 | 1.8 | 0.20094 | 0.076412 | 15.13% | 23.53% | 66.98% | 27.62% | 1.8 | 0.1507 | 0.057309 | 13.85% | 23.14% | 50.23% | 32.4% | 1.4 | 0.12456 | 0.047367 | 11.45% | 31.4% | 53.38% | 64.66%
| N8 - L49 | 14.904 | 0 | 5.93 | 1.361 | 1.113 | 13.063 | 1.8 | 0.018321 | 0.21503 | 15.79% | 25.72% | 71.68% | 26.75% | 1.8 | 0.013741 | 0.16127 | 14.75% | 26.05% | 53.76% | 31.63% | 1.4 | 0.011357 | 0.1333 | 12.19% | 36.33% | 57.13% | 62.87%
| N8 - L50 | 12.609 | 0 | 2.029 | 6.154 | 13.465 | 0.239 | 1.8 | 0.22165 | 0.0039342 | 17.34% | 27.39% | 73.88% | 25.94% | 1.8 | 0.16623 | 0.0029506 | 15.71% | 26.91% | 55.41% | 30.88% | 1.4 | 0.1374 | 0.0024388 | 12.98% | 37.57% | 58.88% | 61.54%
| N8 - L51 | 14.256 | 0 | 11.266 | 0.186 | 0.14 | 17.995 | 1.8 | 0.0023045 | 0.29621 | 29.49% | 39.17% | 98.74% | 29.6% | 1.8 | 0.0017284 | 0.22216 | 27.31% | 40.14% | 74.05% | 33.83% | 1.4 | 0.0014286 | 0.18362 | 22.57% | 59.08% | 78.7% | 67.71%
| N8 - L52 | 11.961 | 0 | 3.308 | 4.607 | 12.211 | 4.692 | 1.8 | 0.201 | 0.077235 | 15.31% | 23.94% | 67% | 27.23% | 1.8 | 0.15075 | 0.057926 | 13.75% | 23.07% | 50.25% | 32.05% | 1.4 | 0.1246 | 0.047878 | 11.36% | 31.23% | 53.4% | 64.08%
| N8 - L53 | 23.183 | 0 | 12.041 | 0.288 | 0.262 | 20.254 | 1.8 | 0.0043128 | 0.3334 | 28.17% | 38.77% | 111.1% | 34.55% | 1.8 | 0.0032346 | 0.25005 | 29.19% | 44.3% | 83.35% | 37.9% | 1.4 | 0.0026735 | 0.20667 | 24.13% | 64.63% | 88.57% | 75.33%
| N8 - L54 | 19.846 | 0 | 0.052 | 6.804 | 18.02 | 0.091 | 1.8 | 0.29663 | 0.0014979 | 16.57% | 31.88% | 98.88% | 31.31% | 1.8 | 0.22247 | 0.0011235 | 16.49% | 34.05% | 74.16% | 35.36% | 1.4 | 0.18388 | 0.00092857 | 13.63% | 46.1% | 78.8% | 70.28%
| N8 - L55 | 15.851 | 0 | 9.892 | 1.021 | 6.056 | 16.553 | 1.8 | 0.099687 | 0.27248 | 25.49% | 34.77% | 90.83% | 32.48% | 1.8 | 0.074765 | 0.20436 | 24.1% | 36.28% | 68.12% | 36.35% | 1.4 | 0.061796 | 0.16891 | 19.92% | 52.97% | 72.39% | 72.85%
| N8 - L56 | 13.231 | 0 | 0.746 | 6.499 | 20.172 | 1.247 | 1.8 | 0.33205 | 0.020527 | 17.36% | 37.62% | 110.7% | 31.78% | 1.8 | 0.24904 | 0.015395 | 15.86% | 36.59% | 83.01% | 35.48% | 1.4 | 0.20584 | 0.012724 | 13.11% | 48.35% | 88.22% | 71.42%
| N9 - L1 | 20.129 | 0 | 7.1 | 1.519 | 0.07 | 14.207 | 1.8 | 0.0011523 | 0.23386 | 17.62% | 26.83% | 77.95% | 28.43% | 1.8 | 0.0008642 | 0.1754 | 17.6% | 29.23% | 58.47% | 33.12% | 1.4 | 0.00071429 | 0.14497 | 14.55% | 41.41% | 62.13% | 65.46%
| N9 - L2 | 14.362 | 0 | 2.321 | 4.146 | 8.956 | 3.808 | 1.8 | 0.14742 | 0.062683 | 12.42% | 17.85% | 49.14% | 25.49% | 1.8 | 0.11057 | 0.047012 | 11.52% | 17.97% | 36.86% | 30.62% | 1.4 | 0.091388 | 0.038857 | 9.519% | 25.14% | 39.17% | 60.75%
| N9 - L3 | 20.66 | 0 | 7.332 | 1.91 | 0.509 | 13.991 | 1.8 | 0.0083786 | 0.2303 | 18.27% | 26.6% | 76.77% | 28.66% | 1.8 | 0.006284 | 0.17273 | 18.36% | 29.25% | 57.58% | 33.34% | 1.4 | 0.0051939 | 0.14277 | 15.18% | 41.77% | 61.19% | 65.85%
| N9 - L4 | 14.893 | 0 | 2.554 | 4.537 | 9.395 | 3.592 | 1.8 | 0.15465 | 0.059128 | 13.51% | 18.8% | 51.55% | 25.77% | 1.8 | 0.11599 | 0.044346 | 12.62% | 19.11% | 38.66% | 30.87% | 1.4 | 0.095867 | 0.036653 | 10.43% | 26.92% | 41.09% | 61.22%
| N9 - L5 | 20.836 | 0 | 2.147 | 0.631 | 1.224 | 10.099 | 1.8 | 0.020148 | 0.16624 | 5.385% | 15.95% | 55.41% | 26.55% | 1.8 | 0.015111 | 0.12468 | 5.424% | 16.8% | 41.56% | 31.63% | 1.4 | 0.01249 | 0.10305 | 4.483% | 20.98% | 44.16% | 62.19%
| N9 - L6 | 15.069 | 0 | 2.632 | 3.258 | 7.662 | 0.3 | 1.8 | 0.12612 | 0.0049383 | 10.85% | 14.81% | 42.04% | 23.36% | 1.8 | 0.094593 | 0.0037037 | 10.15% | 14.98% | 31.53% | 28.73% | 1.4 | 0.078184 | 0.0030612 | 8.391% | 20.67% | 33.51% | 56.68%
| N9 - L7 | 20.075 | 0 | 7.022 | 1.5 | 0.054 | 14.025 | 1.8 | 0.00088889 | 0.23086 | 17.44% | 26.52% | 76.95% | 28.28% | 1.8 | 0.00066667 | 0.17315 | 17.4% | 28.87% | 57.72% | 33% | 1.4 | 0.00055102 | 0.14311 | 14.38% | 40.92% | 61.33% | 65.2%
| N9 - L8 | 14.233 | 0 | 2.246 | 4.053 | 9.217 | 3.668 | 1.8 | 0.15172 | 0.060379 | 12.13% | 18.16% | 50.57% | 25.53% | 1.8 | 0.11379 | 0.045284 | 11.23% | 18.2% | 37.93% | 30.65% | 1.4 | 0.094051 | 0.037429 | 9.283% | 25.25% | 40.31% | 60.83%
| N9 - L9 | 20.59 | 0 | 7.253 | 1.896 | 0.508 | 13.828 | 1.8 | 0.0083621 | 0.22762 | 18.09% | 26.32% | 75.87% | 28.52% | 1.8 | 0.0062716 | 0.17072 | 18.17% | 28.92% | 56.91% | 33.23% | 1.4 | 0.0051837 | 0.1411 | 15.02% | 41.3% | 60.47% | 65.62%
| N9 - L10 | 14.748 | 0 | 2.476 | 4.449 | 9.671 | 3.471 | 1.8 | 0.15919 | 0.057136 | 13.24% | 19.14% | 53.06% | 25.83% | 1.8 | 0.1194 | 0.042852 | 12.34% | 19.37% | 39.8% | 30.91% | 1.4 | 0.098684 | 0.035418 | 10.2% | 27.07% | 42.29% | 61.33%
| N9 - L11 | 20.383 | 0 | 2.219 | 0.352 | 0.266 | 10.016 | 1.8 | 0.0043786 | 0.16487 | 5.437% | 16% | 54.96% | 25.92% | 1.8 | 0.003284 | 0.12365 | 5.446% | 16.78% | 41.22% | 31.06% | 1.4 | 0.0027143 | 0.1022 | 4.501% | 21.07% | 43.8% | 61.05%
| N9 - L12 | 14.541 | 0 | 2.558 | 2.904 | 8.896 | 0.341 | 1.8 | 0.14644 | 0.0056132 | 10.09% | 16.34% | 48.81% | 23.88% | 1.8 | 0.10983 | 0.0042099 | 9.38% | 16.19% | 36.61% | 29.17% | 1.4 | 0.090776 | 0.0034796 | 7.753% | 21.43% | 38.9% | 57.67%
| N9 - L13 | 20.075 | 0 | 7.017 | 1.486 | 0.046 | 14.018 | 1.8 | 0.0007572 | 0.23075 | 17.42% | 26.51% | 76.92% | 28.27% | 1.8 | 0.0005679 | 0.17306 | 17.39% | 28.85% | 57.69% | 32.99% | 1.4 | 0.00046939 | 0.14304 | 14.37% | 40.89% | 61.3% | 65.18%
| N9 - L14 | 14.121 | 0 | 2.241 | 4.295 | 9.709 | 3.673 | 1.8 | 0.15982 | 0.060461 | 12.7% | 19.19% | 53.27% | 25.78% | 1.8 | 0.11986 | 0.045346 | 11.74% | 19.21% | 39.95% | 30.86% | 1.4 | 0.099071 | 0.03748 | 9.705% | 26.67% | 42.46% | 61.3%
| N9 - L15 | 20.582 | 0 | 7.245 | 1.881 | 0.507 | 13.826 | 1.8 | 0.0083457 | 0.22759 | 18.07% | 26.31% | 75.86% | 28.52% | 1.8 | 0.0062593 | 0.17069 | 18.14% | 28.9% | 56.9% | 33.22% | 1.4 | 0.0051735 | 0.14108 | 15% | 41.28% | 60.46% | 65.61%
| N9 - L16 | 14.628 | 0 | 2.469 | 4.689 | 10.17 | 3.481 | 1.8 | 0.16741 | 0.0573 | 13.8% | 20.17% | 55.8% | 26.09% | 1.8 | 0.12556 | 0.042975 | 12.84% | 20.38% | 41.85% | 31.13% | 1.4 | 0.10378 | 0.03552 | 10.62% | 28.5% | 44.48% | 61.81%
| N9 - L17 | 20 | 0 | 2.213 | 1.22 | 1.477 | 10.045 | 1.8 | 0.024313 | 0.16535 | 6.144% | 16.11% | 55.12% | 26.43% | 1.8 | 0.018235 | 0.12401 | 6.125% | 16.81% | 41.34% | 31.51% | 1.4 | 0.015071 | 0.1025 | 5.062% | 21.09% | 43.93% | 62.02%
| N9 - L18 | 14.046 | 0 | 2.563 | 4.029 | 11.141 | 0.3 | 1.8 | 0.18339 | 0.0049383 | 12.53% | 21.04% | 61.13% | 24.96% | 1.8 | 0.13754 | 0.0037037 | 11.57% | 20.81% | 45.85% | 30.09% | 1.4 | 0.11368 | 0.0030612 | 9.566% | 27.99% | 48.72% | 59.69%
| N9 - L19 | 20.075 | 0 | 7.023 | 1.489 | 0.052 | 14.03 | 1.8 | 0.00085597 | 0.23095 | 17.44% | 26.53% | 76.98% | 28.28% | 1.8 | 0.00064198 | 0.17321 | 17.4% | 28.88% | 57.74% | 33% | 1.4 | 0.00053061 | 0.14316 | 14.38% | 40.93% | 61.36% | 65.2%
| N9 - L20 | 14.121 | 0 | 2.247 | 4.298 | 9.716 | 3.685 | 1.8 | 0.15993 | 0.060658 | 12.72% | 19.2% | 53.31% | 25.79% | 1.8 | 0.11995 | 0.045494 | 11.76% | 19.22% | 39.98% | 30.87% | 1.4 | 0.099143 | 0.037602 | 9.716% | 26.69% | 42.49% | 61.31%
| N9 - L21 | 20.577 | 0 | 7.239 | 1.863 | 0.474 | 13.813 | 1.8 | 0.0078025 | 0.22737 | 18.04% | 26.29% | 75.79% | 28.49% | 1.8 | 0.0058519 | 0.17053 | 18.12% | 28.88% | 56.84% | 33.2% | 1.4 | 0.0048367 | 0.14095 | 14.97% | 41.24% | 60.41% | 65.56%
| N9 - L22 | 14.623 | 0 | 2.463 | 4.672 | 10.138 | 3.468 | 1.8 | 0.16688 | 0.057086 | 13.76% | 20.11% | 55.63% | 26.06% | 1.8 | 0.12516 | 0.042815 | 12.8% | 20.32% | 41.72% | 31.11% | 1.4 | 0.10345 | 0.035388 | 10.58% | 28.4% | 44.34% | 61.76%
| N9 - L23 | 20.746 | 0 | 2.255 | 1.777 | 0.419 | 10.142 | 1.8 | 0.0068971 | 0.16695 | 6.916% | 16.13% | 55.65% | 26.16% | 1.8 | 0.0051728 | 0.12521 | 6.959% | 17.01% | 41.74% | 31.27% | 1.4 | 0.0042755 | 0.10349 | 5.752% | 21.36% | 44.35% | 61.46%
| N9 - L24 | 14.792 | 0 | 2.521 | 4.586 | 9.244 | 0.202 | 1.8 | 0.15216 | 0.0033251 | 13.6% | 18.66% | 50.72% | 24.06% | 1.8 | 0.11412 | 0.0024938 | 12.68% | 18.97% | 38.04% | 29.33% | 1.4 | 0.094327 | 0.0020612 | 10.48% | 26.85% | 40.43% | 57.99%
| N9 - L25 | 22.231 | 0 | 5.689 | 1.104 | 0.376 | 12.06 | 1.8 | 0.0061893 | 0.19852 | 13.71% | 21.86% | 66.17% | 27.71% | 1.8 | 0.004642 | 0.14889 | 14.05% | 24.35% | 49.63% | 32.61% | 1.4 | 0.0038367 | 0.12306 | 11.61% | 34.17% | 52.74% | 64.12%
| N9 - L26 | 15.482 | 0 | 0.363 | 4.113 | 10.248 | 0.281 | 1.8 | 0.16869 | 0.0046255 | 10.63% | 19.43% | 56.23% | 24.82% | 1.8 | 0.12652 | 0.0034691 | 10.01% | 19.7% | 42.17% | 30% | 1.4 | 0.10457 | 0.0028673 | 8.272% | 26.93% | 44.82% | 59.34%
| N9 - L27 | 18.366 | 0 | 4.037 | 1.991 | 4.125 | 11.051 | 1.8 | 0.067901 | 0.18191 | 11.17% | 19.77% | 60.64% | 28% | 1.8 | 0.050926 | 0.13643 | 10.91% | 20.7% | 45.48% | 32.83% | 1.4 | 0.042092 | 0.11277 | 9.018% | 27.88% | 48.33% | 65%
| N9 - L28 | 12.38 | 0 | 0.75 | 4.788 | 13.784 | 0.648 | 1.8 | 0.2269 | 0.010667 | 13.01% | 26.4% | 75.63% | 26.28% | 1.8 | 0.17017 | 0.008 | 11.75% | 25.48% | 56.72% | 31.16% | 1.4 | 0.14065 | 0.0066122 | 9.709% | 34.05% | 60.28% | 62.17%
| N9 - L29 | 21.136 | 0 | 7.455 | 1.595 | 0.074 | 14.918 | 1.8 | 0.0012181 | 0.24556 | 18.28% | 27.83% | 81.85% | 29.23% | 1.8 | 0.00091358 | 0.18417 | 18.48% | 30.69% | 61.39% | 33.79% | 1.4 | 0.0007551 | 0.15222 | 15.27% | 43.48% | 65.24% | 66.76%
| N9 - L30 | 15.08 | 0 | 2.437 | 4.353 | 9.404 | 3.998 | 1.8 | 0.1548 | 0.065811 | 12.92% | 18.56% | 51.6% | 26.03% | 1.8 | 0.1161 | 0.049358 | 12.09% | 18.87% | 38.7% | 31.1% | 1.4 | 0.095959 | 0.040796 | 9.994% | 26.4% | 41.13% | 61.69%
| N9 - L31 | 21.693 | 0 | 7.699 | 2.005 | 0.535 | 14.691 | 1.8 | 0.0088066 | 0.24183 | 18.95% | 27.58% | 80.61% | 29.47% | 1.8 | 0.0066049 | 0.18137 | 19.28% | 30.71% | 60.46% | 34.02% | 1.4 | 0.0054592 | 0.14991 | 15.94% | 43.86% | 64.25% | 67.18%
| N9 - L32 | 15.637 | 0 | 2.681 | 4.764 | 9.864 | 3.771 | 1.8 | 0.16237 | 0.062074 | 14.05% | 19.55% | 54.12% | 26.33% | 1.8 | 0.12178 | 0.046556 | 13.25% | 20.07% | 40.59% | 31.36% | 1.4 | 0.10065 | 0.03848 | 10.95% | 28.27% | 43.14% | 62.19%
| N9 - L33 | 21.878 | 0 | 2.254 | 0.662 | 1.285 | 10.604 | 1.8 | 0.021152 | 0.17455 | 5.582% | 16.53% | 58.18% | 27.16% | 1.8 | 0.015864 | 0.13091 | 5.694% | 17.64% | 43.64% | 32.16% | 1.4 | 0.013112 | 0.1082 | 4.706% | 22.03% | 46.37% | 63.21%
| N9 - L34 | 15.823 | 0 | 2.763 | 3.421 | 8.045 | 0.315 | 1.8 | 0.13243 | 0.0051852 | 11.27% | 15.4% | 44.14% | 23.74% | 1.8 | 0.099321 | 0.0038889 | 10.66% | 15.73% | 33.11% | 29.08% | 1.4 | 0.082092 | 0.0032143 | 8.81% | 21.7% | 35.18% | 57.34%
| N9 - L35 | 21.079 | 0 | 7.373 | 1.575 | 0.056 | 14.726 | 1.8 | 0.00092181 | 0.2424 | 18.09% | 27.5% | 80.8% | 29.06% | 1.8 | 0.00069136 | 0.1818 | 18.27% | 30.31% | 60.6% | 33.66% | 1.4 | 0.00057143 | 0.15027 | 15.1% | 42.96% | 64.4% | 66.48%
| N9 - L36 | 14.945 | 0 | 2.358 | 4.256 | 9.677 | 3.851 | 1.8 | 0.15929 | 0.063391 | 12.62% | 18.89% | 53.1% | 26.08% | 1.8 | 0.11947 | 0.047543 | 11.79% | 19.11% | 39.82% | 31.13% | 1.4 | 0.098745 | 0.039296 | 9.747% | 26.51% | 42.32% | 61.78%
| N9 - L37 | 21.62 | 0 | 7.615 | 1.991 | 0.533 | 14.519 | 1.8 | 0.0087737 | 0.239 | 18.76% | 27.29% | 79.67% | 29.32% | 1.8 | 0.0065802 | 0.17925 | 19.08% | 30.36% | 59.75% | 33.9% | 1.4 | 0.0054388 | 0.14815 | 15.77% | 43.37% | 63.49% | 66.93%
| N9 - L38 | 15.486 | 0 | 2.6 | 4.671 | 10.154 | 3.644 | 1.8 | 0.16714 | 0.059984 | 13.77% | 19.9% | 55.71% | 26.4% | 1.8 | 0.12536 | 0.044988 | 12.96% | 20.34% | 41.79% | 31.41% | 1.4 | 0.10361 | 0.037184 | 10.71% | 28.42% | 44.41% | 62.31%
| N9 - L39 | 21.402 | 0 | 2.33 | 0.369 | 0.28 | 10.517 | 1.8 | 0.0046091 | 0.17312 | 5.638% | 16.59% | 57.71% | 26.48% | 1.8 | 0.0034568 | 0.12984 | 5.718% | 17.62% | 43.28% | 31.56% | 1.4 | 0.0028571 | 0.10732 | 4.726% | 22.12% | 45.99% | 62%
| N9 - L40 | 15.268 | 0 | 2.685 | 3.049 | 9.341 | 0.358 | 1.8 | 0.15376 | 0.005893 | 10.49% | 17% | 51.25% | 24.3% | 1.8 | 0.11532 | 0.0044198 | 9.847% | 17% | 38.44% | 29.56% | 1.4 | 0.095316 | 0.0036531 | 8.139% | 22.51% | 40.85% | 58.41%
| N9 - L41 | 21.079 | 0 | 7.368 | 1.56 | 0.048 | 14.719 | 1.8 | 0.00079012 | 0.24229 | 18.07% | 27.49% | 80.76% | 29.05% | 1.8 | 0.00059259 | 0.18172 | 18.25% | 30.3% | 60.57% | 33.65% | 1.4 | 0.0004898 | 0.15019 | 15.09% | 42.94% | 64.37% | 66.47%
| N9 - L42 | 14.827 | 0 | 2.353 | 4.509 | 10.195 | 3.857 | 1.8 | 0.16782 | 0.06349 | 13.21% | 19.96% | 55.94% | 26.35% | 1.8 | 0.12586 | 0.047617 | 12.33% | 20.17% | 41.95% | 31.36% | 1.4 | 0.10403 | 0.039357 | 10.19% | 28.01% | 44.58% | 62.28%
| N9 - L43 | 21.611 | 0 | 7.607 | 1.975 | 0.532 | 14.517 | 1.8 | 0.0087572 | 0.23896 | 18.73% | 27.28% | 79.65% | 29.31% | 1.8 | 0.0065679 | 0.17922 | 19.05% | 30.35% | 59.74% | 33.89% | 1.4 | 0.0054286 | 0.14813 | 15.74% | 43.34% | 63.49% | 66.92%
| N9 - L44 | 15.359 | 0 | 2.592 | 4.924 | 10.679 | 3.655 | 1.8 | 0.17579 | 0.060165 | 14.35% | 20.98% | 58.6% | 26.68% | 1.8 | 0.13184 | 0.045123 | 13.49% | 21.4% | 43.95% | 31.65% | 1.4 | 0.10897 | 0.037296 | 11.15% | 29.92% | 46.7% | 62.83%
| N9 - L45 | 21 | 0 | 2.324 | 1.281 | 1.551 | 10.547 | 1.8 | 0.025531 | 0.17361 | 6.373% | 16.7% | 57.87% | 27.03% | 1.8 | 0.019148 | 0.13021 | 6.432% | 17.66% | 43.4% | 32.04% | 1.4 | 0.015827 | 0.10762 | 5.316% | 22.15% | 46.12% | 63.04%
| N9 - L46 | 14.748 | 0 | 2.691 | 4.23 | 11.698 | 0.314 | 1.8 | 0.19256 | 0.0051687 | 13.04% | 21.89% | 64.19% | 25.48% | 1.8 | 0.14442 | 0.0038765 | 12.15% | 21.85% | 48.14% | 30.55% | 1.4 | 0.11937 | 0.0032041 | 10.04% | 29.38% | 51.16% | 60.58%
| N9 - L47 | 21.078 | 0 | 7.374 | 1.564 | 0.055 | 14.731 | 1.8 | 0.00090535 | 0.24249 | 18.09% | 27.51% | 80.83% | 29.06% | 1.8 | 0.00067901 | 0.18186 | 18.27% | 30.32% | 60.62% | 33.66% | 1.4 | 0.00056122 | 0.15032 | 15.1% | 42.97% | 64.42% | 66.49%
| N9 - L48 | 14.827 | 0 | 2.359 | 4.513 | 10.201 | 3.87 | 1.8 | 0.16792 | 0.063704 | 13.23% | 19.97% | 55.97% | 26.36% | 1.8 | 0.12594 | 0.047778 | 12.34% | 20.18% | 41.98% | 31.37% | 1.4 | 0.10409 | 0.03949 | 10.2% | 28.03% | 44.61% | 62.3%
| N9 - L49 | 21.606 | 0 | 7.601 | 1.956 | 0.498 | 14.503 | 1.8 | 0.0081975 | 0.23873 | 18.71% | 27.26% | 79.58% | 29.28% | 1.8 | 0.0061481 | 0.17905 | 19.02% | 30.32% | 59.68% | 33.87% | 1.4 | 0.0050816 | 0.14799 | 15.72% | 43.3% | 63.42% | 66.87%
| N9 - L50 | 15.354 | 0 | 2.586 | 4.905 | 10.644 | 3.641 | 1.8 | 0.17521 | 0.059934 | 14.3% | 20.91% | 58.4% | 26.65% | 1.8 | 0.13141 | 0.044951 | 13.44% | 21.33% | 43.8% | 31.63% | 1.4 | 0.10861 | 0.037153 | 11.11% | 29.82% | 46.55% | 62.78%
| N9 - L51 | 21.783 | 0 | 2.368 | 1.866 | 0.44 | 10.65 | 1.8 | 0.0072428 | 0.17531 | 7.172% | 16.73% | 58.44% | 26.74% | 1.8 | 0.0054321 | 0.13148 | 7.307% | 17.86% | 43.83% | 31.79% | 1.4 | 0.0044898 | 0.10867 | 6.04% | 22.43% | 46.57% | 62.44%
| N9 - L52 | 15.531 | 0 | 2.647 | 4.815 | 9.706 | 0.212 | 1.8 | 0.15977 | 0.0034897 | 14.14% | 19.4% | 53.26% | 24.5% | 1.8 | 0.11983 | 0.0026173 | 13.32% | 19.92% | 39.94% | 29.73% | 1.4 | 0.099041 | 0.0021633 | 11.01% | 28.19% | 42.45% | 58.75%
| N9 - L53 | 31.124 | 0 | 7.964 | 1.545 | 0.527 | 16.885 | 1.8 | 0.0086749 | 0.27794 | 17.34% | 27.64% | 92.65% | 34.01% | 1.8 | 0.0065062 | 0.20846 | 19.66% | 34.09% | 69.49% | 37.89% | 1.4 | 0.0053776 | 0.1723 | 16.25% | 47.83% | 73.84% | 74.31%
| N9 - L54 | 21.674 | 0 | 0.509 | 5.759 | 14.347 | 0.393 | 1.8 | 0.23616 | 0.0064691 | 13.77% | 25.16% | 78.72% | 29.13% | 1.8 | 0.17712 | 0.0048519 | 14.01% | 27.58% | 59.04% | 33.75% | 1.4 | 0.1464 | 0.0040102 | 11.58% | 37.7% | 62.74% | 66.6%
| N9 - L55 | 22.039 | 0 | 4.844 | 2.389 | 4.95 | 13.261 | 1.8 | 0.081481 | 0.21829 | 12.81% | 22.67% | 72.76% | 31.08% | 1.8 | 0.061111 | 0.16372 | 13.09% | 24.84% | 54.57% | 35.45% | 1.4 | 0.05051 | 0.13532 | 10.82% | 33.45% | 57.99% | 70.14%
| N9 - L56 | 14.856 | 0 | 0.9 | 5.746 | 16.541 | 0.777 | 1.8 | 0.27228 | 0.01279 | 15.1% | 30.64% | 90.76% | 28.99% | 1.8 | 0.20421 | 0.0095926 | 14.1% | 30.57% | 68.07% | 33.41% | 1.4 | 0.16879 | 0.0079286 | 11.65% | 40.86% | 72.34% | 66.71%
| N10 - L1 | 19.971 | 0 | 7.092 | 1.519 | 0.071 | 14.209 | 1.8 | 0.0011687 | 0.23389 | 17.64% | 26.88% | 77.96% | 28.39% | 1.8 | 0.00087654 | 0.17542 | 17.58% | 29.22% | 58.47% | 33.08% | 1.4 | 0.00072449 | 0.14499 | 14.53% | 41.39% | 62.14% | 65.39%
| N10 - L2 | 18.712 | 0 | 2.299 | 3.19 | 8.21 | 3.589 | 1.8 | 0.13514 | 0.059078 | 9.715% | 14.83% | 45.05% | 26.1% | 1.8 | 0.10136 | 0.044309 | 9.531% | 15.64% | 33.79% | 31.23% | 1.4 | 0.083776 | 0.036622 | 7.877% | 21.27% | 35.9% | 61.57%
| N10 - L3 | 20.502 | 0 | 7.325 | 1.91 | 0.51 | 13.994 | 1.8 | 0.0083951 | 0.23035 | 18.29% | 26.65% | 76.78% | 28.62% | 1.8 | 0.0062963 | 0.17277 | 18.35% | 29.24% | 57.59% | 33.3% | 1.4 | 0.0052041 | 0.1428 | 15.17% | 41.76% | 61.2% | 65.78%
| N10 - L4 | 19.243 | 0 | 2.531 | 2.799 | 7.772 | 3.373 | 1.8 | 0.12793 | 0.055523 | 9.262% | 13.71% | 42.64% | 25.88% | 1.8 | 0.095951 | 0.041642 | 9.147% | 14.5% | 31.98% | 31.05% | 1.4 | 0.079306 | 0.034418 | 7.56% | 19.49% | 33.99% | 61.14%
| N10 - L5 | 20.678 | 0 | 2.139 | 0.631 | 1.223 | 10.102 | 1.8 | 0.020132 | 0.16629 | 5.377% | 15.97% | 55.43% | 26.51% | 1.8 | 0.015099 | 0.12472 | 5.405% | 16.79% | 41.57% | 31.59% | 1.4 | 0.01248 | 0.10308 | 4.468% | 20.96% | 44.18% | 62.13%
| N10 - L6 | 19.419 | 0 | 2.654 | 4.078 | 9.504 | 0.518 | 1.8 | 0.15644 | 0.0085267 | 11.92% | 17.41% | 52.15% | 25.5% | 1.8 | 0.11733 | 0.0063951 | 11.79% | 18.63% | 39.11% | 30.69% | 1.4 | 0.09698 | 0.0052857 | 9.747% | 25.74% | 41.56% | 60.36%
| N10 - L7 | 19.969 | 0 | 7.089 | 1.507 | 0.068 | 14.208 | 1.8 | 0.0011193 | 0.23388 | 17.63% | 26.88% | 77.96% | 28.39% | 1.8 | 0.00083951 | 0.17541 | 17.57% | 29.21% | 58.47% | 33.08% | 1.4 | 0.00069388 | 0.14498 | 14.52% | 41.38% | 62.13% | 65.39%
| N10 - L8 | 18.823 | 0 | 2.299 | 3.448 | 8.712 | 3.58 | 1.8 | 0.14341 | 0.05893 | 10.22% | 15.78% | 47.8% | 26.41% | 1.8 | 0.10756 | 0.044198 | 10.04% | 16.68% | 35.85% | 31.5% | 1.4 | 0.088898 | 0.036531 | 8.302% | 22.75% | 38.1% | 62.12%
| N10 - L9 | 20.508 | 0 | 7.324 | 1.883 | 0.479 | 13.989 | 1.8 | 0.0078848 | 0.23027 | 18.27% | 26.64% | 76.76% | 28.6% | 1.8 | 0.0059136 | 0.1727 | 18.33% | 29.24% | 57.57% | 33.28% | 1.4 | 0.0048878 | 0.14274 | 15.15% | 41.74% | 61.18% | 65.75%
| N10 - L10 | 19.362 | 0 | 2.534 | 3.072 | 8.301 | 3.361 | 1.8 | 0.13664 | 0.055325 | 9.759% | 14.71% | 45.55% | 26.2% | 1.8 | 0.10248 | 0.041494 | 9.652% | 15.6% | 34.16% | 31.33% | 1.4 | 0.084704 | 0.034296 | 7.978% | 21.06% | 36.3% | 61.71%
| N10 - L11 | 21.063 | 0 | 2.137 | 0.237 | 2.933 | 10.059 | 1.8 | 0.04828 | 0.16558 | 5.16% | 15.84% | 55.19% | 27.46% | 1.8 | 0.03621 | 0.12419 | 5.211% | 16.73% | 41.4% | 32.43% | 1.4 | 0.029929 | 0.10264 | 4.307% | 20.89% | 43.99% | 63.86%
| N10 - L12 | 19.917 | 0 | 2.653 | 5.192 | 11.714 | 0.569 | 1.8 | 0.19282 | 0.0093663 | 14.19% | 21.5% | 64.27% | 26.97% | 1.8 | 0.14462 | 0.0070247 | 14.13% | 23.19% | 48.21% | 31.94% | 1.4 | 0.11953 | 0.0058061 | 11.68% | 32.21% | 51.23% | 62.96%
| N10 - L13 | 19.915 | 0 | 7.017 | 1.491 | 0.058 | 14.038 | 1.8 | 0.00095473 | 0.23108 | 17.46% | 26.59% | 77.03% | 28.25% | 1.8 | 0.00071605 | 0.17331 | 17.39% | 28.88% | 57.77% | 32.97% | 1.4 | 0.00059184 | 0.14324 | 14.37% | 40.92% | 61.39% | 65.15%
| N10 - L14 | 18.907 | 0 | 2.241 | 3.377 | 8.993 | 3.48 | 1.8 | 0.14803 | 0.057284 | 9.989% | 16.08% | 49.34% | 26.54% | 1.8 | 0.11102 | 0.042963 | 9.824% | 16.97% | 37.01% | 31.61% | 1.4 | 0.091765 | 0.03551 | 8.119% | 22.95% | 39.33% | 62.35%
| N10 - L15 | 20.433 | 0 | 7.238 | 1.851 | 0.445 | 13.812 | 1.8 | 0.0073251 | 0.22736 | 18.07% | 26.33% | 75.79% | 28.44% | 1.8 | 0.0054938 | 0.17052 | 18.11% | 28.88% | 56.84% | 33.15% | 1.4 | 0.0045408 | 0.14094 | 14.97% | 41.24% | 60.4% | 65.47%
| N10 - L16 | 19.426 | 0 | 2.463 | 3.017 | 8.606 | 3.254 | 1.8 | 0.14166 | 0.053564 | 9.537% | 15.06% | 47.22% | 26.34% | 1.8 | 0.10625 | 0.040173 | 9.44% | 15.94% | 35.42% | 31.45% | 1.4 | 0.087816 | 0.033204 | 7.802% | 21.34% | 37.64% | 61.95%
| N10 - L17 | 21.356 | 0 | 2.25 | 0.04 | 3.873 | 10.073 | 1.8 | 0.063753 | 0.16581 | 5.381% | 15.92% | 55.27% | 28.06% | 1.8 | 0.047815 | 0.12436 | 5.454% | 16.9% | 41.45% | 32.96% | 1.4 | 0.03952 | 0.10279 | 4.508% | 21.24% | 44.05% | 64.92%
| N10 - L18 | 20.348 | 0 | 2.526 | 4.828 | 12.924 | 0.485 | 1.8 | 0.21274 | 0.0079835 | 13.19% | 22.67% | 70.91% | 27.83% | 1.8 | 0.15956 | 0.0059877 | 13.21% | 24.35% | 53.19% | 32.65% | 1.4 | 0.13188 | 0.004949 | 10.92% | 32.92% | 56.52% | 64.43%
| N10 - L19 | 19.917 | 0 | 7.015 | 1.489 | 0.053 | 14.032 | 1.8 | 0.00087243 | 0.23098 | 17.45% | 26.57% | 76.99% | 28.24% | 1.8 | 0.00065432 | 0.17323 | 17.38% | 28.87% | 57.74% | 32.96% | 1.4 | 0.00054082 | 0.14318 | 14.37% | 40.91% | 61.36% | 65.14%
| N10 - L20 | 18.909 | 0 | 2.239 | 3.379 | 8.998 | 3.474 | 1.8 | 0.14812 | 0.057185 | 9.99% | 16.09% | 49.37% | 26.54% | 1.8 | 0.11109 | 0.042889 | 9.825% | 16.98% | 37.03% | 31.61% | 1.4 | 0.091816 | 0.035449 | 8.121% | 22.97% | 39.35% | 62.35%
| N10 - L21 | 20.419 | 0 | 7.231 | 1.863 | 0.475 | 13.815 | 1.8 | 0.0078189 | 0.22741 | 18.06% | 26.33% | 75.8% | 28.45% | 1.8 | 0.0058642 | 0.17056 | 18.1% | 28.87% | 56.85% | 33.16% | 1.4 | 0.0048469 | 0.14097 | 14.96% | 41.22% | 60.42% | 65.5%
| N10 - L22 | 19.411 | 0 | 2.456 | 3.005 | 8.577 | 3.257 | 1.8 | 0.14119 | 0.053613 | 9.505% | 15.01% | 47.06% | 26.32% | 1.8 | 0.10589 | 0.04021 | 9.407% | 15.89% | 35.3% | 31.43% | 1.4 | 0.08752 | 0.033235 | 7.775% | 21.26% | 37.51% | 61.92%
| N10 - L23 | 20.588 | 0 | 2.247 | 1.777 | 0.419 | 10.145 | 1.8 | 0.0068971 | 0.167 | 6.915% | 16.16% | 55.67% | 26.12% | 1.8 | 0.0051728 | 0.12525 | 6.944% | 17% | 41.75% | 31.24% | 1.4 | 0.0042755 | 0.10352 | 5.739% | 21.34% | 44.37% | 61.4%
| N10 - L24 | 19.58 | 0 | 2.528 | 3.091 | 9.47 | 0.413 | 1.8 | 0.15588 | 0.0067984 | 9.759% | 16.31% | 51.96% | 25.48% | 1.8 | 0.11691 | 0.0050988 | 9.679% | 17.23% | 38.97% | 30.66% | 1.4 | 0.096633 | 0.0042143 | 8% | 22.82% | 41.41% | 60.3%
| N10 - L25 | 22.073 | 0 | 5.681 | 1.104 | 0.376 | 12.063 | 1.8 | 0.0061893 | 0.19857 | 13.72% | 21.9% | 66.19% | 27.67% | 1.8 | 0.004642 | 0.14893 | 14.03% | 24.34% | 49.64% | 32.57% | 1.4 | 0.0038367 | 0.12309 | 11.59% | 34.15% | 52.75% | 64.06%
| N10 - L26 | 20.732 | 0 | 0.351 | 4.328 | 10.382 | 0.035 | 1.8 | 0.1709 | 0.00057613 | 10.46% | 18.58% | 56.97% | 26.11% | 1.8 | 0.12817 | 0.0004321 | 10.52% | 20.18% | 42.72% | 31.23% | 1.4 | 0.10594 | 0.00035714 | 8.699% | 27.75% | 45.4% | 61.37%
| N10 - L27 | 20.797 | 0 | 4.294 | 0.015 | 5.055 | 11.052 | 1.8 | 0.08321 | 0.18193 | 10.34% | 19.45% | 60.64% | 29.21% | 1.8 | 0.062407 | 0.13644 | 10.41% | 21.05% | 45.48% | 33.92% | 1.4 | 0.051582 | 0.11278 | 8.602% | 28.63% | 48.33% | 67.01%
| N10 - L28 | 19.757 | 0 | 0.492 | 4.895 | 14.111 | 0.435 | 1.8 | 0.23228 | 0.0071605 | 12% | 24.54% | 77.43% | 28.45% | 1.8 | 0.17421 | 0.0053704 | 11.92% | 26.07% | 58.07% | 33.14% | 1.4 | 0.14399 | 0.0044388 | 9.856% | 34.84% | 61.71% | 65.53%
| N10 - L29 | 20.97 | 0 | 7.447 | 1.595 | 0.074 | 14.92 | 1.8 | 0.0012181 | 0.2456 | 18.3% | 27.88% | 81.87% | 29.18% | 1.8 | 0.00091358 | 0.1842 | 18.46% | 30.68% | 61.4% | 33.75% | 1.4 | 0.0007551 | 0.15224 | 15.26% | 43.46% | 65.25% | 66.69%
| N10 - L30 | 19.648 | 0 | 2.414 | 3.349 | 8.621 | 3.768 | 1.8 | 0.14191 | 0.062025 | 10.08% | 15.39% | 47.3% | 26.67% | 1.8 | 0.10643 | 0.046519 | 10.01% | 16.42% | 35.48% | 31.74% | 1.4 | 0.087969 | 0.038449 | 8.271% | 22.33% | 37.7% | 62.55%
| N10 - L31 | 21.527 | 0 | 7.691 | 2.005 | 0.535 | 14.693 | 1.8 | 0.0088066 | 0.24186 | 18.97% | 27.63% | 80.62% | 29.42% | 1.8 | 0.0066049 | 0.1814 | 19.26% | 30.71% | 60.47% | 33.98% | 1.4 | 0.0054592 | 0.14993 | 15.92% | 43.84% | 64.26% | 67.11%
| N10 - L32 | 20.205 | 0 | 2.658 | 2.939 | 8.16 | 3.542 | 1.8 | 0.13432 | 0.058305 | 9.61% | 14.22% | 44.77% | 26.43% | 1.8 | 0.10074 | 0.043728 | 9.605% | 15.22% | 33.58% | 31.55% | 1.4 | 0.083265 | 0.036143 | 7.939% | 20.46% | 35.69% | 62.08%
| N10 - L33 | 21.712 | 0 | 2.246 | 0.662 | 1.284 | 10.607 | 1.8 | 0.021136 | 0.1746 | 5.575% | 16.56% | 58.2% | 27.12% | 1.8 | 0.015852 | 0.13095 | 5.675% | 17.63% | 43.65% | 32.13% | 1.4 | 0.013102 | 0.10823 | 4.691% | 22.01% | 46.39% | 63.15%
| N10 - L34 | 20.39 | 0 | 2.787 | 4.282 | 9.98 | 0.544 | 1.8 | 0.16428 | 0.0089547 | 12.36% | 18.06% | 54.76% | 26.03% | 1.8 | 0.12321 | 0.006716 | 12.38% | 19.56% | 41.07% | 31.16% | 1.4 | 0.10184 | 0.005551 | 10.24% | 27.03% | 43.64% | 61.26%
| N10 - L35 | 20.968 | 0 | 7.444 | 1.582 | 0.072 | 14.918 | 1.8 | 0.0011852 | 0.24556 | 18.28% | 27.87% | 81.85% | 29.18% | 1.8 | 0.00088889 | 0.18417 | 18.45% | 30.67% | 61.39% | 33.75% | 1.4 | 0.00073469 | 0.15222 | 15.25% | 43.45% | 65.24% | 66.69%
| N10 - L36 | 19.764 | 0 | 2.414 | 3.62 | 9.148 | 3.759 | 1.8 | 0.15058 | 0.061877 | 10.61% | 16.37% | 50.19% | 27.01% | 1.8 | 0.11294 | 0.046407 | 10.55% | 17.51% | 37.65% | 32.03% | 1.4 | 0.093347 | 0.038357 | 8.717% | 23.89% | 40.01% | 63.14%
| N10 - L37 | 21.533 | 0 | 7.69 | 1.977 | 0.503 | 14.689 | 1.8 | 0.0082798 | 0.24179 | 18.95% | 27.62% | 80.6% | 29.4% | 1.8 | 0.0062099 | 0.18135 | 19.25% | 30.7% | 60.45% | 33.96% | 1.4 | 0.0051327 | 0.14989 | 15.91% | 43.83% | 64.24% | 67.07%
| N10 - L38 | 20.33 | 0 | 2.661 | 3.225 | 8.716 | 3.529 | 1.8 | 0.14347 | 0.058091 | 10.12% | 15.26% | 47.82% | 26.78% | 1.8 | 0.1076 | 0.043568 | 10.13% | 16.38% | 35.87% | 31.85% | 1.4 | 0.088939 | 0.03601 | 8.376% | 22.11% | 38.12% | 62.7%
| N10 - L39 | 22.117 | 0 | 2.244 | 0.249 | 3.08 | 10.562 | 1.8 | 0.0507 | 0.17386 | 5.349% | 16.42% | 57.95% | 28.14% | 1.8 | 0.038025 | 0.1304 | 5.472% | 17.57% | 43.47% | 33.03% | 1.4 | 0.031429 | 0.10778 | 4.523% | 21.94% | 46.19% | 65%
| N10 - L40 | 20.913 | 0 | 2.786 | 5.451 | 12.3 | 0.598 | 1.8 | 0.20247 | 0.0098436 | 14.72% | 22.3% | 67.49% | 27.63% | 1.8 | 0.15185 | 0.0073827 | 14.84% | 24.35% | 50.62% | 32.51% | 1.4 | 0.12551 | 0.006102 | 12.26% | 33.82% | 53.79% | 64.06%
| N10 - L41 | 20.911 | 0 | 7.368 | 1.566 | 0.061 | 14.74 | 1.8 | 0.0010041 | 0.24263 | 18.11% | 27.57% | 80.88% | 29.03% | 1.8 | 0.00075309 | 0.18198 | 18.26% | 30.33% | 60.66% | 33.62% | 1.4 | 0.00062245 | 0.15041 | 15.09% | 42.97% | 64.46% | 66.43%
| N10 - L42 | 19.852 | 0 | 2.353 | 3.546 | 9.443 | 3.654 | 1.8 | 0.15544 | 0.060148 | 10.37% | 16.68% | 51.81% | 27.15% | 1.8 | 0.11658 | 0.045111 | 10.31% | 17.82% | 38.86% | 32.15% | 1.4 | 0.096357 | 0.037286 | 8.526% | 24.1% | 41.3% | 63.39%
| N10 - L43 | 21.455 | 0 | 7.6 | 1.944 | 0.468 | 14.503 | 1.8 | 0.0077037 | 0.23873 | 18.74% | 27.31% | 79.58% | 29.23% | 1.8 | 0.0057778 | 0.17905 | 19.01% | 30.32% | 59.68% | 33.82% | 1.4 | 0.0047755 | 0.14799 | 15.72% | 43.3% | 63.42% | 66.77%
| N10 - L44 | 20.397 | 0 | 2.586 | 3.168 | 9.036 | 3.417 | 1.8 | 0.14874 | 0.056247 | 9.894% | 15.63% | 49.58% | 26.93% | 1.8 | 0.11156 | 0.042185 | 9.912% | 16.74% | 37.19% | 31.97% | 1.4 | 0.092204 | 0.034867 | 8.193% | 22.41% | 39.52% | 62.95%
| N10 - L45 | 22.423 | 0 | 2.363 | 0.042 | 4.066 | 10.577 | 1.8 | 0.06693 | 0.17411 | 5.579% | 16.5% | 58.04% | 28.78% | 1.8 | 0.050198 | 0.13058 | 5.728% | 17.75% | 43.53% | 33.59% | 1.4 | 0.04149 | 0.10793 | 4.735% | 22.31% | 46.26% | 66.14%
| N10 - L46 | 21.365 | 0 | 2.652 | 5.069 | 13.57 | 0.509 | 1.8 | 0.22337 | 0.0083786 | 13.68% | 23.51% | 74.46% | 28.56% | 1.8 | 0.16753 | 0.006284 | 13.87% | 25.57% | 55.84% | 33.28% | 1.4 | 0.13847 | 0.0051939 | 11.46% | 34.56% | 59.34% | 65.64%
| N10 - L47 | 20.912 | 0 | 7.366 | 1.564 | 0.056 | 14.734 | 1.8 | 0.00092181 | 0.24253 | 18.1% | 27.56% | 80.84% | 29.02% | 1.8 | 0.00069136 | 0.1819 | 18.25% | 30.32% | 60.63% | 33.62% | 1.4 | 0.00057143 | 0.15035 | 15.09% | 42.95% | 64.43% | 66.42%
| N10 - L48 | 19.854 | 0 | 2.351 | 3.548 | 9.448 | 3.648 | 1.8 | 0.15552 | 0.060049 | 10.37% | 16.69% | 51.84% | 27.15% | 1.8 | 0.11664 | 0.045037 | 10.32% | 17.83% | 38.88% | 32.15% | 1.4 | 0.096408 | 0.037224 | 8.527% | 24.12% | 41.32% | 63.39%
| N10 - L49 | 21.44 | 0 | 7.593 | 1.956 | 0.498 | 14.506 | 1.8 | 0.0081975 | 0.23878 | 18.73% | 27.31% | 79.59% | 29.24% | 1.8 | 0.0061481 | 0.17909 | 19% | 30.31% | 59.7% | 33.83% | 1.4 | 0.0050816 | 0.14802 | 15.71% | 43.28% | 63.44% | 66.8%
| N10 - L50 | 20.382 | 0 | 2.578 | 3.155 | 9.005 | 3.42 | 1.8 | 0.14823 | 0.056296 | 9.859% | 15.57% | 49.41% | 26.91% | 1.8 | 0.11117 | 0.042222 | 9.875% | 16.68% | 37.06% | 31.96% | 1.4 | 0.091888 | 0.034898 | 8.162% | 22.33% | 39.38% | 62.92%
| N10 - L51 | 21.617 | 0 | 2.36 | 1.866 | 0.44 | 10.652 | 1.8 | 0.0072428 | 0.17534 | 7.171% | 16.76% | 58.45% | 26.7% | 1.8 | 0.0054321 | 0.13151 | 7.292% | 17.85% | 43.84% | 31.75% | 1.4 | 0.0044898 | 0.10869 | 6.027% | 22.41% | 46.58% | 62.38%
| N10 - L52 | 20.559 | 0 | 2.655 | 3.246 | 9.944 | 0.433 | 1.8 | 0.16369 | 0.0071276 | 10.13% | 16.92% | 54.56% | 26% | 1.8 | 0.12277 | 0.0053457 | 10.16% | 18.09% | 40.92% | 31.14% | 1.4 | 0.10147 | 0.0044184 | 8.401% | 23.96% | 43.49% | 61.19%
| N10 - L53 | 30.903 | 0 | 7.954 | 1.545 | 0.526 | 16.888 | 1.8 | 0.0086584 | 0.27799 | 17.36% | 27.71% | 92.66% | 33.94% | 1.8 | 0.0064938 | 0.20849 | 19.64% | 34.08% | 69.5% | 37.83% | 1.4 | 0.0053673 | 0.17233 | 16.23% | 47.81% | 73.85% | 74.21%
| N10 - L54 | 29.025 | 0 | 0.491 | 6.059 | 14.534 | 0.049 | 1.8 | 0.23924 | 0.00080658 | 13.29% | 23.61% | 79.75% | 31.15% | 1.8 | 0.17943 | 0.00060494 | 14.73% | 28.25% | 59.81% | 35.59% | 1.4 | 0.14831 | 0.0005 | 12.18% | 38.85% | 63.56% | 69.67%
| N10 - L55 | 24.956 | 0 | 5.153 | 0.019 | 6.066 | 13.263 | 1.8 | 0.099852 | 0.21832 | 11.8% | 22.2% | 72.77% | 32.69% | 1.8 | 0.074889 | 0.16374 | 12.49% | 25.26% | 54.58% | 36.85% | 1.4 | 0.061898 | 0.13534 | 10.32% | 34.36% | 58% | 72.74%
| N10 - L56 | 23.709 | 0 | 0.59 | 5.874 | 16.933 | 0.523 | 1.8 | 0.27873 | 0.0086091 | 13.72% | 28.07% | 92.91% | 31.82% | 1.8 | 0.20905 | 0.0064568 | 14.31% | 31.29% | 69.68% | 35.92% | 1.4 | 0.17279 | 0.0053367 | 11.83% | 41.81% | 74.05% | 71%
| N11 - L1 | 14.978 | 0 | 10.878 | 0.121 | 0.137 | 17.337 | 1.8 | 0.0022551 | 0.28538 | 28.2% | 37.41% | 95.13% | 29.3% | 1.8 | 0.0016914 | 0.21404 | 26.37% | 38.7% | 71.35% | 33.63% | 1.4 | 0.001398 | 0.17691 | 21.79% | 56.99% | 75.82% | 67.17%
| N11 - L2 | 17.391 | 0 | 3.19 | 4.5 | 11.027 | 4.485 | 1.8 | 0.18151 | 0.073827 | 13.86% | 20.48% | 60.5% | 27.91% | 1.8 | 0.13614 | 0.05537 | 13.37% | 21.3% | 45.38% | 32.74% | 1.4 | 0.11252 | 0.045765 | 11.05% | 29.19% | 48.22% | 64.91%
| N11 - L3 | 14.169 | 0 | 5.628 | 0.154 | 0.136 | 12.529 | 1.8 | 0.0022387 | 0.20624 | 14.75% | 24.84% | 68.75% | 25.74% | 1.8 | 0.001679 | 0.15468 | 13.65% | 24.91% | 51.56% | 30.75% | 1.4 | 0.0013878 | 0.12785 | 11.28% | 34.67% | 54.79% | 61.07%
| N11 - L4 | 16.582 | 0 | 2.06 | 4.532 | 11.026 | 0.323 | 1.8 | 0.1815 | 0.0053169 | 12.64% | 20.73% | 60.5% | 25.56% | 1.8 | 0.13612 | 0.0039877 | 12.07% | 21.34% | 45.37% | 30.67% | 1.4 | 0.11251 | 0.0032959 | 9.973% | 29.29% | 48.22% | 60.62%
| N11 - L5 | 13.539 | 0 | 10.909 | 0.179 | 0.134 | 17.423 | 1.8 | 0.0022058 | 0.2868 | 28.83% | 38.3% | 95.6% | 28.93% | 1.8 | 0.0016543 | 0.2151 | 26.44% | 38.86% | 71.7% | 33.29% | 1.4 | 0.0013673 | 0.17779 | 21.86% | 57.2% | 76.19% | 66.62%
| N11 - L6 | 15.951 | 0 | 3.221 | 4.558 | 11.024 | 4.572 | 1.8 | 0.18147 | 0.075259 | 14.29% | 20.92% | 60.49% | 27.55% | 1.8 | 0.1361 | 0.056444 | 13.53% | 21.37% | 45.37% | 32.41% | 1.4 | 0.11249 | 0.046653 | 11.18% | 29.36% | 48.21% | 64.37%
| N11 - L7 | 14.986 | 0 | 10.881 | 0.13 | 0.157 | 17.338 | 1.8 | 0.0025844 | 0.2854 | 28.21% | 37.41% | 95.13% | 29.31% | 1.8 | 0.0019383 | 0.21405 | 26.38% | 38.71% | 71.35% | 33.64% | 1.4 | 0.001602 | 0.17692 | 21.8% | 57% | 75.82% | 67.2%
| N11 - L8 | 17.488 | 0 | 3.193 | 4.803 | 11.657 | 4.488 | 1.8 | 0.19188 | 0.073877 | 14.47% | 21.67% | 63.96% | 28.35% | 1.8 | 0.14391 | 0.055407 | 13.98% | 22.58% | 47.97% | 33.1% | 1.4 | 0.11895 | 0.045796 | 11.55% | 31% | 50.98% | 65.67%
| N11 - L9 | 14.475 | 0 | 5.626 | 1.164 | 2.225 | 12.527 | 1.8 | 0.036626 | 0.20621 | 14.99% | 24.74% | 68.74% | 26.85% | 1.8 | 0.027469 | 0.15465 | 13.93% | 24.9% | 51.55% | 31.73% | 1.4 | 0.022704 | 0.12783 | 11.51% | 34.66% | 54.78% | 63.12%
| N11 - L10 | 16.976 | 0 | 2.061 | 5.837 | 13.725 | 0.323 | 1.8 | 0.22593 | 0.0053169 | 15.64% | 25.88% | 75.31% | 27.36% | 1.8 | 0.16944 | 0.0039877 | 15% | 26.83% | 56.48% | 32.16% | 1.4 | 0.14005 | 0.0032959 | 12.4% | 37.02% | 60.02% | 63.77%
| N11 - L11 | 13.541 | 0 | 10.906 | 0.184 | 0.146 | 17.424 | 1.8 | 0.0024033 | 0.28681 | 28.83% | 38.29% | 95.6% | 28.93% | 1.8 | 0.0018025 | 0.21511 | 26.44% | 38.86% | 71.7% | 33.29% | 1.4 | 0.0014898 | 0.1778 | 21.85% | 57.2% | 76.2% | 66.64%
| N11 - L12 | 16.042 | 0 | 3.219 | 4.858 | 11.645 | 4.574 | 1.8 | 0.19169 | 0.075292 | 14.9% | 22.12% | 63.9% | 27.98% | 1.8 | 0.14377 | 0.056469 | 14.13% | 22.64% | 47.92% | 32.76% | 1.4 | 0.11883 | 0.046673 | 11.67% | 31.14% | 50.93% | 65.11%
| N11 - L13 | 14.966 | 0 | 10.733 | 0.136 | 0.169 | 17.1 | 1.8 | 0.0027819 | 0.28148 | 27.83% | 36.91% | 93.83% | 29.13% | 1.8 | 0.0020864 | 0.21111 | 26.02% | 38.18% | 70.37% | 33.5% | 1.4 | 0.0017245 | 0.17449 | 21.5% | 56.22% | 74.78% | 66.89%
| N11 - L14 | 17.564 | 0 | 3.082 | 4.684 | 11.931 | 4.327 | 1.8 | 0.1964 | 0.071226 | 14.06% | 21.91% | 65.47% | 28.46% | 1.8 | 0.1473 | 0.05342 | 13.59% | 22.79% | 49.1% | 33.19% | 1.4 | 0.12174 | 0.044153 | 11.23% | 31.05% | 52.18% | 65.86%
| N11 - L15 | 14.801 | 0 | 5.652 | 0.725 | 3.118 | 12.448 | 1.8 | 0.051325 | 0.20491 | 14.81% | 24.54% | 68.3% | 27.35% | 1.8 | 0.038494 | 0.15368 | 13.81% | 24.83% | 51.23% | 32.18% | 1.4 | 0.031816 | 0.12702 | 11.42% | 34.62% | 54.44% | 64.04%
| N11 - L16 | 17.398 | 0 | 1.999 | 5.273 | 14.881 | 0.324 | 1.8 | 0.24495 | 0.0053333 | 14.17% | 26.78% | 81.65% | 28.27% | 1.8 | 0.18372 | 0.004 | 13.67% | 27.65% | 61.24% | 32.92% | 1.4 | 0.15185 | 0.0033061 | 11.3% | 37.07% | 65.08% | 65.33%
| N11 - L17 | 13.58 | 0 | 10.73 | 0.191 | 0.163 | 17.15 | 1.8 | 0.0026831 | 0.2823 | 28.35% | 37.67% | 94.1% | 28.74% | 1.8 | 0.0020123 | 0.21173 | 26.01% | 38.24% | 70.58% | 33.15% | 1.4 | 0.0016633 | 0.175 | 21.5% | 56.28% | 75% | 66.32%
| N11 - L18 | 16.178 | 0 | 3.08 | 4.739 | 11.926 | 4.377 | 1.8 | 0.19631 | 0.072049 | 14.42% | 22.36% | 65.44% | 28.09% | 1.8 | 0.14723 | 0.054037 | 13.7% | 22.86% | 49.08% | 32.85% | 1.4 | 0.12169 | 0.044663 | 11.32% | 31.2% | 52.15% | 65.3%
| N11 - L19 | 14.954 | 0 | 10.726 | 0.122 | 0.137 | 17.097 | 1.8 | 0.0022551 | 0.28143 | 27.82% | 36.9% | 93.81% | 29.1% | 1.8 | 0.0016914 | 0.21107 | 26% | 38.17% | 70.36% | 33.48% | 1.4 | 0.001398 | 0.17446 | 21.49% | 56.19% | 74.77% | 66.85%
| N11 - L20 | 17.552 | 0 | 3.076 | 4.67 | 11.9 | 4.325 | 1.8 | 0.19588 | 0.071193 | 14.02% | 21.86% | 65.29% | 28.44% | 1.8 | 0.14691 | 0.053395 | 13.55% | 22.73% | 48.97% | 33.17% | 1.4 | 0.12143 | 0.044133 | 11.2% | 30.96% | 52.04% | 65.82%
| N11 - L21 | 14.194 | 0 | 5.652 | 1.296 | 1.061 | 12.449 | 1.8 | 0.017465 | 0.20492 | 15.19% | 24.74% | 68.31% | 26.14% | 1.8 | 0.013099 | 0.15369 | 14.05% | 24.83% | 51.23% | 31.11% | 1.4 | 0.010827 | 0.12703 | 11.62% | 34.63% | 54.44% | 61.83%
| N11 - L22 | 16.792 | 0 | 1.999 | 3.252 | 10.702 | 0.324 | 1.8 | 0.17616 | 0.0053333 | 9.665% | 18.83% | 58.72% | 25.43% | 1.8 | 0.13212 | 0.004 | 9.252% | 19.14% | 44.04% | 30.56% | 1.4 | 0.1092 | 0.0033061 | 7.647% | 25.08% | 46.8% | 60.37%
| N11 - L23 | 13.577 | 0 | 10.734 | 0.177 | 0.133 | 17.145 | 1.8 | 0.0021893 | 0.28222 | 28.36% | 37.66% | 94.07% | 28.72% | 1.8 | 0.001642 | 0.21167 | 26.02% | 38.24% | 70.56% | 33.13% | 1.4 | 0.0013571 | 0.17495 | 21.51% | 56.29% | 74.98% | 66.28%
| N11 - L24 | 16.175 | 0 | 3.083 | 4.725 | 11.896 | 4.373 | 1.8 | 0.19582 | 0.071984 | 14.4% | 22.3% | 65.27% | 28.07% | 1.8 | 0.14686 | 0.053988 | 13.67% | 22.8% | 48.95% | 32.83% | 1.4 | 0.12139 | 0.044622 | 11.3% | 31.12% | 52.02% | 65.26%
| N11 - L25 | 16.56 | 0 | 8.604 | 0.205 | 0.187 | 14.475 | 1.8 | 0.0030782 | 0.23827 | 21.86% | 30.08% | 79.42% | 27.68% | 1.8 | 0.0023086 | 0.1787 | 20.86% | 31.66% | 59.57% | 32.41% | 1.4 | 0.0019082 | 0.1477 | 17.24% | 46.19% | 63.3% | 64.35%
| N11 - L26 | 19.423 | 0 | 0.111 | 5.251 | 13.244 | 0.173 | 1.8 | 0.21801 | 0.0028477 | 12.86% | 23.81% | 72.67% | 27.63% | 1.8 | 0.16351 | 0.0021358 | 12.73% | 25.37% | 54.5% | 32.46% | 1.4 | 0.13514 | 0.0017653 | 10.52% | 34.62% | 57.92% | 64.12%
| N11 - L27 | 15.428 | 0 | 8.1 | 1.145 | 5.316 | 13.577 | 1.8 | 0.087506 | 0.22349 | 21.08% | 28.66% | 74.5% | 29.55% | 1.8 | 0.06563 | 0.16762 | 19.83% | 29.74% | 55.87% | 34.03% | 1.4 | 0.054245 | 0.13854 | 16.39% | 43.41% | 59.37% | 67.91%
| N11 - L28 | 18.027 | 0 | 0.407 | 5.693 | 17.079 | 0.719 | 1.8 | 0.28114 | 0.011835 | 14.22% | 30.11% | 93.71% | 30.33% | 1.8 | 0.21085 | 0.0088765 | 13.83% | 31.24% | 70.28% | 34.57% | 1.4 | 0.17428 | 0.0073367 | 11.43% | 41.49% | 74.69% | 68.8%
| N11 - L29 | 15.727 | 0 | 11.422 | 0.127 | 0.144 | 18.204 | 1.8 | 0.0023704 | 0.29965 | 29.32% | 38.89% | 99.88% | 30.23% | 1.8 | 0.0017778 | 0.22474 | 27.69% | 40.64% | 74.91% | 34.37% | 1.4 | 0.0014694 | 0.18576 | 22.88% | 59.84% | 79.61% | 68.68%
| N11 - L30 | 18.26 | 0 | 3.35 | 4.725 | 11.578 | 4.71 | 1.8 | 0.19058 | 0.077531 | 14.39% | 21.27% | 63.53% | 28.64% | 1.8 | 0.14294 | 0.058148 | 14.04% | 22.36% | 47.65% | 33.37% | 1.4 | 0.11814 | 0.048061 | 11.6% | 30.65% | 50.63% | 66.15%
| N11 - L31 | 14.878 | 0 | 5.909 | 0.162 | 0.143 | 13.155 | 1.8 | 0.0023539 | 0.21654 | 15.35% | 25.84% | 72.18% | 26.32% | 1.8 | 0.0017654 | 0.16241 | 14.33% | 26.15% | 54.14% | 31.25% | 1.4 | 0.0014592 | 0.13423 | 11.84% | 36.4% | 57.53% | 62.07%
| N11 - L32 | 17.411 | 0 | 2.163 | 4.759 | 11.577 | 0.339 | 1.8 | 0.19057 | 0.0055802 | 13.13% | 21.53% | 63.52% | 26.11% | 1.8 | 0.14293 | 0.0041852 | 12.67% | 22.41% | 47.64% | 31.15% | 1.4 | 0.11813 | 0.0034592 | 10.47% | 30.75% | 50.63% | 61.56%
| N11 - L33 | 14.216 | 0 | 11.454 | 0.188 | 0.141 | 18.294 | 1.8 | 0.002321 | 0.30114 | 30% | 39.85% | 100.4% | 29.83% | 1.8 | 0.0017407 | 0.22585 | 27.77% | 40.81% | 75.28% | 34.01% | 1.4 | 0.0014388 | 0.18667 | 22.95% | 60.06% | 80% | 68.1%
| N11 - L34 | 16.749 | 0 | 3.382 | 4.786 | 11.575 | 4.8 | 1.8 | 0.19053 | 0.079012 | 14.85% | 21.74% | 63.51% | 28.26% | 1.8 | 0.1429 | 0.059259 | 14.2% | 22.44% | 47.63% | 33.02% | 1.4 | 0.11811 | 0.04898 | 11.74% | 30.83% | 50.62% | 65.58%
| N11 - L35 | 15.736 | 0 | 11.425 | 0.137 | 0.165 | 18.205 | 1.8 | 0.002716 | 0.29967 | 29.33% | 38.89% | 99.89% | 30.24% | 1.8 | 0.002037 | 0.22475 | 27.69% | 40.64% | 74.92% | 34.38% | 1.4 | 0.0016837 | 0.18577 | 22.89% | 59.85% | 79.61% | 68.71%
| N11 - L36 | 18.362 | 0 | 3.353 | 5.043 | 12.239 | 4.712 | 1.8 | 0.20147 | 0.077564 | 15.03% | 22.5% | 67.16% | 29.12% | 1.8 | 0.1511 | 0.058173 | 14.68% | 23.71% | 50.37% | 33.76% | 1.4 | 0.12489 | 0.048082 | 12.13% | 32.54% | 53.52% | 66.97%
| N11 - L37 | 15.199 | 0 | 5.908 | 1.222 | 2.337 | 13.153 | 1.8 | 0.038469 | 0.21651 | 15.6% | 25.72% | 72.17% | 27.51% | 1.8 | 0.028852 | 0.16238 | 14.62% | 26.15% | 54.13% | 32.3% | 1.4 | 0.023847 | 0.13421 | 12.09% | 36.4% | 57.52% | 64.26%
| N11 - L38 | 17.825 | 0 | 2.164 | 6.129 | 14.411 | 0.34 | 1.8 | 0.23722 | 0.0055967 | 16.24% | 26.88% | 79.07% | 28.07% | 1.8 | 0.17791 | 0.0041975 | 15.75% | 28.18% | 59.3% | 32.77% | 1.4 | 0.14705 | 0.0034694 | 13.02% | 38.88% | 63.02% | 64.96%
| N11 - L39 | 14.218 | 0 | 11.451 | 0.194 | 0.153 | 18.295 | 1.8 | 0.0025185 | 0.30115 | 29.99% | 39.84% | 100.4% | 29.84% | 1.8 | 0.0018889 | 0.22586 | 27.76% | 40.8% | 75.29% | 34.02% | 1.4 | 0.0015612 | 0.18668 | 22.94% | 60.05% | 80.01% | 68.11%
| N11 - L40 | 16.844 | 0 | 3.38 | 5.1 | 12.227 | 4.802 | 1.8 | 0.20127 | 0.079045 | 15.48% | 22.99% | 67.09% | 28.72% | 1.8 | 0.15095 | 0.059284 | 14.83% | 23.77% | 50.32% | 33.4% | 1.4 | 0.12477 | 0.049 | 12.26% | 32.69% | 53.47% | 66.38%
| N11 - L41 | 15.715 | 0 | 11.269 | 0.143 | 0.177 | 17.955 | 1.8 | 0.0029136 | 0.29556 | 28.94% | 38.37% | 98.52% | 30.04% | 1.8 | 0.0021852 | 0.22167 | 27.32% | 40.09% | 73.89% | 34.23% | 1.4 | 0.0018061 | 0.18321 | 22.58% | 59.03% | 78.52% | 68.37%
| N11 - L42 | 18.442 | 0 | 3.236 | 4.918 | 12.528 | 4.544 | 1.8 | 0.20622 | 0.074798 | 14.6% | 22.75% | 68.74% | 29.24% | 1.8 | 0.15467 | 0.056099 | 14.27% | 23.93% | 51.56% | 33.86% | 1.4 | 0.12784 | 0.046367 | 11.79% | 32.6% | 54.79% | 67.18%
| N11 - L43 | 15.541 | 0 | 5.934 | 0.761 | 3.274 | 13.071 | 1.8 | 0.053893 | 0.21516 | 15.4% | 25.52% | 71.72% | 28.06% | 1.8 | 0.04042 | 0.16137 | 14.5% | 26.07% | 53.79% | 32.78% | 1.4 | 0.033408 | 0.13338 | 11.99% | 36.35% | 57.16% | 65.24%
| N11 - L44 | 18.268 | 0 | 2.099 | 5.537 | 15.625 | 0.34 | 1.8 | 0.2572 | 0.0055967 | 14.71% | 27.81% | 85.73% | 29.07% | 1.8 | 0.1929 | 0.0041975 | 14.35% | 29.03% | 64.3% | 33.58% | 1.4 | 0.15944 | 0.0034694 | 11.86% | 38.92% | 68.33% | 66.65%
| N11 - L45 | 14.259 | 0 | 11.267 | 0.2 | 0.172 | 18.007 | 1.8 | 0.0028313 | 0.29641 | 29.49% | 39.19% | 98.8% | 29.63% | 1.8 | 0.0021235 | 0.22231 | 27.31% | 40.16% | 74.1% | 33.86% | 1.4 | 0.0017551 | 0.18374 | 22.58% | 59.1% | 78.75% | 67.76%
| N11 - L46 | 16.987 | 0 | 3.234 | 4.976 | 12.522 | 4.596 | 1.8 | 0.20612 | 0.075654 | 14.99% | 23.23% | 68.71% | 28.85% | 1.8 | 0.15459 | 0.056741 | 14.38% | 24% | 51.53% | 33.5% | 1.4 | 0.12778 | 0.046898 | 11.89% | 32.76% | 54.76% | 66.58%
| N11 - L47 | 15.702 | 0 | 11.263 | 0.128 | 0.144 | 17.952 | 1.8 | 0.0023704 | 0.29551 | 28.93% | 38.37% | 98.5% | 30.01% | 1.8 | 0.0017778 | 0.22163 | 27.3% | 40.08% | 73.88% | 34.2% | 1.4 | 0.0014694 | 0.18318 | 22.57% | 59.01% | 78.51% | 68.33%
| N11 - L48 | 18.429 | 0 | 3.23 | 4.904 | 12.495 | 4.541 | 1.8 | 0.20568 | 0.074749 | 14.56% | 22.7% | 68.56% | 29.22% | 1.8 | 0.15426 | 0.056062 | 14.23% | 23.87% | 51.42% | 33.84% | 1.4 | 0.1275 | 0.046337 | 11.76% | 32.51% | 54.64% | 67.13%
| N11 - L49 | 14.904 | 0 | 5.934 | 1.361 | 1.114 | 13.071 | 1.8 | 0.018337 | 0.21516 | 15.8% | 25.73% | 71.72% | 26.75% | 1.8 | 0.013753 | 0.16137 | 14.76% | 26.07% | 53.79% | 31.64% | 1.4 | 0.011367 | 0.13338 | 12.2% | 36.35% | 57.16% | 62.88%
| N11 - L50 | 17.631 | 0 | 2.098 | 3.415 | 11.237 | 0.34 | 1.8 | 0.18497 | 0.0055967 | 10.04% | 19.56% | 61.66% | 25.97% | 1.8 | 0.13873 | 0.0041975 | 9.715% | 20.1% | 46.24% | 31.03% | 1.4 | 0.11466 | 0.0034694 | 8.029% | 26.34% | 49.14% | 61.29%
| N11 - L51 | 14.256 | 0 | 11.27 | 0.186 | 0.14 | 18.003 | 1.8 | 0.0023045 | 0.29635 | 29.5% | 39.19% | 98.78% | 29.61% | 1.8 | 0.0017284 | 0.22226 | 27.32% | 40.16% | 74.09% | 33.84% | 1.4 | 0.0014286 | 0.1837 | 22.58% | 59.1% | 78.73% | 67.72%
| N11 - L52 | 16.984 | 0 | 3.237 | 4.962 | 12.491 | 4.592 | 1.8 | 0.20561 | 0.075588 | 14.96% | 23.17% | 68.54% | 28.82% | 1.8 | 0.15421 | 0.056691 | 14.36% | 23.94% | 51.4% | 33.48% | 1.4 | 0.12746 | 0.046857 | 11.87% | 32.67% | 54.63% | 66.53%
| N11 - L53 | 23.183 | 0 | 12.046 | 0.288 | 0.262 | 20.265 | 1.8 | 0.0043128 | 0.33358 | 28.19% | 38.79% | 111.2% | 34.56% | 1.8 | 0.0032346 | 0.25019 | 29.21% | 44.32% | 83.4% | 37.91% | 1.4 | 0.0026735 | 0.20679 | 24.14% | 64.66% | 88.62% | 75.35%
| N11 - L54 | 27.192 | 0 | 0.156 | 7.352 | 18.542 | 0.242 | 1.8 | 0.30522 | 0.0039835 | 16.42% | 30.39% | 101.7% | 34.15% | 1.8 | 0.22891 | 0.0029877 | 17.82% | 35.52% | 76.3% | 37.8% | 1.4 | 0.1892 | 0.0024694 | 14.73% | 48.46% | 81.09% | 74.61%
| N11 - L55 | 18.513 | 0 | 9.72 | 1.374 | 6.379 | 16.293 | 1.8 | 0.105 | 0.2682 | 24.32% | 33.06% | 89.4% | 33.36% | 1.8 | 0.078753 | 0.20115 | 23.79% | 35.68% | 67.05% | 37.13% | 1.4 | 0.065092 | 0.16626 | 19.67% | 52.09% | 71.25% | 74.17%
| N11 - L56 | 21.633 | 0 | 0.489 | 6.832 | 20.494 | 0.863 | 1.8 | 0.33735 | 0.014206 | 16.32% | 34.55% | 112.4% | 34.66% | 1.8 | 0.25301 | 0.010654 | 16.6% | 37.48% | 84.34% | 37.94% | 1.4 | 0.20912 | 0.0088061 | 13.72% | 49.79% | 89.62% | 75.61%
| N12 - L1 | 9.163 | 0 | 0.694 | 0.392 | 0.268 | 8.977 | 1.8 | 0.0044115 | 0.14777 | 2.238% | 15.09% | 49.26% | 22.56% | 1.8 | 0.0033086 | 0.11083 | 1.932% | 13.27% | 36.94% | 27.91% | 1.4 | 0.0027347 | 0.091602 | 1.597% | 15.11% | 39.26% | 55.58%
| N12 - L2 | 14.446 | 0 | 3.14 | 3.846 | 9.426 | 0.681 | 1.8 | 0.15516 | 0.01121 | 12.96% | 18.19% | 51.72% | 24.28% | 1.8 | 0.11637 | 0.0084074 | 12.03% | 18.21% | 38.79% | 29.53% | 1.4 | 0.096184 | 0.006949 | 9.947% | 24.95% | 41.22% | 58.44%
| N12 - L3 | 9.441 | 0 | 5.711 | 0.372 | 0.233 | 12.737 | 1.8 | 0.0038354 | 0.20966 | 16.01% | 26.94% | 69.89% | 24.64% | 1.8 | 0.0028765 | 0.15725 | 13.87% | 25.31% | 52.42% | 29.71% | 1.4 | 0.0023776 | 0.12997 | 11.47% | 35.22% | 55.7% | 59.41%
| N12 - L4 | 14.724 | 0 | 1.877 | 3.826 | 9.391 | 3.08 | 1.8 | 0.15458 | 0.0507 | 11.09% | 18.05% | 51.53% | 25.47% | 1.8 | 0.11594 | 0.038025 | 10.33% | 18.13% | 38.65% | 30.6% | 1.4 | 0.095827 | 0.031429 | 8.538% | 24.84% | 41.07% | 60.66%
| N12 - L5 | 9.895 | 0 | 5.616 | 0.352 | 0.224 | 13.123 | 1.8 | 0.0036872 | 0.21602 | 15.64% | 27.26% | 72.01% | 24.99% | 1.8 | 0.0027654 | 0.16201 | 13.64% | 25.71% | 54% | 30.01% | 1.4 | 0.0022857 | 0.13391 | 11.27% | 35.5% | 57.39% | 60%
| N12 - L6 | 15.178 | 0 | 1.782 | 3.806 | 9.382 | 3.466 | 1.8 | 0.15444 | 0.057053 | 10.87% | 17.91% | 51.48% | 25.77% | 1.8 | 0.11583 | 0.04279 | 10.19% | 18.09% | 38.61% | 30.88% | 1.4 | 0.095735 | 0.035367 | 8.419% | 24.77% | 41.03% | 61.2%
| N12 - L7 | 9.474 | 0 | 0.696 | 1.409 | 2.374 | 8.973 | 1.8 | 0.039078 | 0.1477 | 4.394% | 15.02% | 49.23% | 23.54% | 1.8 | 0.029309 | 0.11078 | 3.809% | 13.26% | 36.93% | 28.82% | 1.4 | 0.024224 | 0.091561 | 3.148% | 15.11% | 39.24% | 57.47%
| N12 - L8 | 14.849 | 0 | 3.139 | 5.159 | 12.143 | 0.687 | 1.8 | 0.19988 | 0.011309 | 15.68% | 23.53% | 66.63% | 25.95% | 1.8 | 0.14991 | 0.0084815 | 14.64% | 23.73% | 49.97% | 30.95% | 1.4 | 0.12391 | 0.0070102 | 12.1% | 32.74% | 53.1% | 61.43%
| N12 - L9 | 9.446 | 0 | 5.71 | 0.378 | 0.246 | 12.741 | 1.8 | 0.0040494 | 0.20973 | 16.01% | 26.95% | 69.91% | 24.65% | 1.8 | 0.003037 | 0.1573 | 13.87% | 25.31% | 52.43% | 29.72% | 1.4 | 0.0025102 | 0.13001 | 11.46% | 35.22% | 55.72% | 59.42%
| N12 - L10 | 14.822 | 0 | 1.874 | 4.127 | 10.015 | 3.081 | 1.8 | 0.16486 | 0.050716 | 11.78% | 19.28% | 54.95% | 25.85% | 1.8 | 0.12364 | 0.038037 | 10.99% | 19.4% | 41.21% | 30.93% | 1.4 | 0.10219 | 0.031439 | 9.08% | 26.63% | 43.8% | 61.35%
| N12 - L11 | 9.896 | 0 | 5.608 | 0.351 | 0.222 | 13.107 | 1.8 | 0.0036543 | 0.21575 | 15.62% | 27.23% | 71.92% | 24.98% | 1.8 | 0.0027407 | 0.16181 | 13.62% | 25.67% | 53.94% | 30.01% | 1.4 | 0.0022653 | 0.13374 | 11.26% | 35.46% | 57.32% | 59.98%
| N12 - L12 | 15.272 | 0 | 1.772 | 4.1 | 9.99 | 3.447 | 1.8 | 0.16444 | 0.056741 | 11.53% | 19.1% | 54.81% | 26.14% | 1.8 | 0.12333 | 0.042556 | 10.83% | 19.33% | 41.11% | 31.19% | 1.4 | 0.10194 | 0.035173 | 8.948% | 26.52% | 43.69% | 61.86%
| N12 - L13 | 9.865 | 0 | 0.791 | 0.977 | 3.284 | 8.939 | 1.8 | 0.054058 | 0.14714 | 3.495% | 15% | 49.05% | 24.04% | 1.8 | 0.040543 | 0.11036 | 3.047% | 13.35% | 36.79% | 29.28% | 1.4 | 0.03351 | 0.091214 | 2.518% | 15.34% | 39.09% | 58.4%
| N12 - L14 | 15.3 | 0 | 3.038 | 4.602 | 13.316 | 0.666 | 1.8 | 0.21919 | 0.010963 | 14.24% | 24.5% | 73.06% | 26.8% | 1.8 | 0.1644 | 0.0082222 | 13.37% | 24.58% | 54.8% | 31.67% | 1.4 | 0.13588 | 0.0067959 | 11.05% | 32.83% | 58.23% | 62.91%
| N12 - L15 | 9.512 | 0 | 5.635 | 0.383 | 0.263 | 12.583 | 1.8 | 0.0043292 | 0.20713 | 15.78% | 26.58% | 69.04% | 24.58% | 1.8 | 0.0032469 | 0.15535 | 13.69% | 24.99% | 51.78% | 29.67% | 1.4 | 0.0026837 | 0.1284 | 11.31% | 34.77% | 55.03% | 59.3%
| N12 - L16 | 14.947 | 0 | 1.806 | 4.009 | 10.295 | 2.978 | 1.8 | 0.16947 | 0.049021 | 11.4% | 19.52% | 56.49% | 25.99% | 1.8 | 0.1271 | 0.036765 | 10.66% | 19.62% | 42.37% | 31.05% | 1.4 | 0.10505 | 0.030388 | 8.809% | 26.7% | 45.02% | 61.6%
| N12 - L17 | 9.948 | 0 | 5.53 | 0.347 | 0.217 | 12.921 | 1.8 | 0.003572 | 0.21269 | 15.39% | 26.83% | 70.9% | 24.88% | 1.8 | 0.002679 | 0.15952 | 13.43% | 25.31% | 53.17% | 29.92% | 1.4 | 0.0022143 | 0.13185 | 11.1% | 34.96% | 56.51% | 59.8%
| N12 - L18 | 15.384 | 0 | 1.701 | 3.972 | 10.249 | 3.316 | 1.8 | 0.16871 | 0.054584 | 11.14% | 19.31% | 56.24% | 26.26% | 1.8 | 0.12653 | 0.040938 | 10.47% | 19.51% | 42.18% | 31.29% | 1.4 | 0.10458 | 0.033837 | 8.656% | 26.52% | 44.82% | 62.06%
| N12 - L19 | 9.241 | 0 | 0.783 | 1.061 | 0.933 | 8.938 | 1.8 | 0.015358 | 0.14713 | 3.699% | 15.12% | 49.04% | 22.84% | 1.8 | 0.011519 | 0.11035 | 3.196% | 13.33% | 36.78% | 28.17% | 1.4 | 0.0095204 | 0.091204 | 2.642% | 15.31% | 39.09% | 56.12%
| N12 - L20 | 14.676 | 0 | 3.046 | 2.564 | 9.099 | 0.667 | 1.8 | 0.14978 | 0.010979 | 10.36% | 16.24% | 49.93% | 24.16% | 1.8 | 0.11233 | 0.0082346 | 9.65% | 16% | 37.44% | 29.43% | 1.4 | 0.092847 | 0.0068061 | 7.976% | 20.74% | 39.79% | 58.2%
| N12 - L21 | 9.498 | 0 | 5.641 | 0.37 | 0.232 | 12.578 | 1.8 | 0.0038189 | 0.20705 | 15.8% | 26.59% | 69.02% | 24.56% | 1.8 | 0.0028642 | 0.15528 | 13.7% | 24.99% | 51.76% | 29.65% | 1.4 | 0.0023673 | 0.12835 | 11.33% | 34.78% | 55.01% | 59.26%
| N12 - L22 | 14.934 | 0 | 1.812 | 3.995 | 10.263 | 2.973 | 1.8 | 0.16894 | 0.048938 | 11.38% | 19.47% | 56.31% | 25.97% | 1.8 | 0.1267 | 0.036704 | 10.63% | 19.56% | 42.23% | 31.03% | 1.4 | 0.10472 | 0.030337 | 8.788% | 26.61% | 44.88% | 61.56%
| N12 - L23 | 9.946 | 0 | 5.543 | 0.35 | 0.223 | 12.948 | 1.8 | 0.0036708 | 0.21314 | 15.42% | 26.88% | 71.05% | 24.89% | 1.8 | 0.0027531 | 0.15985 | 13.46% | 25.36% | 53.28% | 29.94% | 1.4 | 0.0022755 | 0.13212 | 11.13% | 35.03% | 56.62% | 59.83%
| N12 - L24 | 15.382 | 0 | 1.714 | 3.975 | 10.255 | 3.343 | 1.8 | 0.16881 | 0.055029 | 11.16% | 19.32% | 56.27% | 26.27% | 1.8 | 0.1266 | 0.041272 | 10.49% | 19.52% | 42.2% | 31.3% | 1.4 | 0.10464 | 0.034112 | 8.672% | 26.54% | 44.85% | 62.09%
| N12 - L25 | 12.133 | 0 | 4.051 | 0.411 | 0.282 | 10.82 | 1.8 | 0.004642 | 0.17811 | 10.97% | 21.13% | 59.37% | 24.28% | 1.8 | 0.0034815 | 0.13358 | 9.869% | 20.4% | 44.53% | 29.47% | 1.4 | 0.0028776 | 0.11041 | 8.157% | 27.58% | 47.32% | 58.57%
| N12 - L26 | 18.297 | 0 | 0.217 | 4.388 | 11.338 | 0.137 | 1.8 | 0.18663 | 0.0022551 | 10.91% | 20.56% | 62.21% | 26.11% | 1.8 | 0.13998 | 0.0016914 | 10.65% | 21.57% | 46.66% | 31.16% | 1.4 | 0.11569 | 0.001398 | 8.801% | 29.32% | 49.58% | 61.49%
| N12 - L27 | 11.387 | 0 | 3.95 | 1.334 | 5.4 | 10.247 | 1.8 | 0.088889 | 0.16867 | 11.35% | 20.35% | 56.22% | 26.24% | 1.8 | 0.066667 | 0.12651 | 10.11% | 19.47% | 42.17% | 31.22% | 1.4 | 0.055102 | 0.10456 | 8.352% | 26.45% | 44.81% | 62.36%
| N12 - L28 | 16.852 | 0 | 0.113 | 4.958 | 15.431 | 0.585 | 1.8 | 0.25401 | 0.0096296 | 12.55% | 27.42% | 84.67% | 28.65% | 1.8 | 0.19051 | 0.0072222 | 12.02% | 27.97% | 63.5% | 33.21% | 1.4 | 0.15746 | 0.0059694 | 9.935% | 36.95% | 67.48% | 66.02%
| N12 - L29 | 9.621 | 0 | 0.728 | 0.411 | 0.281 | 9.425 | 1.8 | 0.0046255 | 0.15514 | 2.332% | 15.74% | 51.71% | 22.9% | 1.8 | 0.0034691 | 0.11636 | 2.026% | 13.93% | 38.79% | 28.22% | 1.4 | 0.0028673 | 0.096173 | 1.675% | 15.86% | 41.22% | 56.19%
| N12 - L30 | 15.168 | 0 | 3.297 | 4.038 | 9.897 | 0.715 | 1.8 | 0.16291 | 0.01177 | 13.48% | 18.92% | 54.3% | 24.74% | 1.8 | 0.12219 | 0.0088272 | 12.64% | 19.12% | 40.73% | 29.94% | 1.4 | 0.10099 | 0.0072959 | 10.44% | 26.2% | 43.28% | 59.23%
| N12 - L31 | 9.913 | 0 | 5.997 | 0.391 | 0.244 | 13.374 | 1.8 | 0.0040165 | 0.22015 | 16.7% | 28.1% | 73.38% | 25.15% | 1.8 | 0.0030123 | 0.16511 | 14.57% | 26.57% | 55.04% | 30.15% | 1.4 | 0.0024898 | 0.13647 | 12.04% | 36.98% | 58.49% | 60.3%
| N12 - L32 | 15.46 | 0 | 1.971 | 4.018 | 9.86 | 3.234 | 1.8 | 0.1623 | 0.053235 | 11.53% | 18.77% | 54.1% | 26.01% | 1.8 | 0.12173 | 0.039926 | 10.85% | 19.04% | 40.58% | 31.08% | 1.4 | 0.10061 | 0.033 | 8.966% | 26.09% | 43.12% | 61.6%
| N12 - L33 | 10.389 | 0 | 5.896 | 0.37 | 0.235 | 13.779 | 1.8 | 0.0038683 | 0.22681 | 16.3% | 28.43% | 75.6% | 25.53% | 1.8 | 0.0029012 | 0.17011 | 14.32% | 26.99% | 56.7% | 30.48% | 1.4 | 0.002398 | 0.1406 | 11.84% | 37.28% | 60.26% | 60.94%
| N12 - L34 | 15.937 | 0 | 1.871 | 3.996 | 9.851 | 3.639 | 1.8 | 0.16216 | 0.059901 | 11.3% | 18.62% | 54.05% | 26.34% | 1.8 | 0.12162 | 0.044926 | 10.69% | 18.99% | 40.54% | 31.37% | 1.4 | 0.10052 | 0.037133 | 8.839% | 26.01% | 43.08% | 62.17%
| N12 - L35 | 9.947 | 0 | 0.731 | 1.48 | 2.492 | 9.422 | 1.8 | 0.041021 | 0.15509 | 4.584% | 15.67% | 51.7% | 23.95% | 1.8 | 0.030765 | 0.11632 | 4.001% | 13.93% | 38.77% | 29.19% | 1.4 | 0.025429 | 0.096143 | 3.307% | 15.87% | 41.2% | 58.2%
| N12 - L36 | 15.592 | 0 | 3.296 | 5.416 | 12.75 | 0.721 | 1.8 | 0.20988 | 0.011868 | 16.3% | 24.47% | 69.96% | 26.54% | 1.8 | 0.15741 | 0.0089012 | 15.37% | 24.92% | 52.47% | 31.47% | 1.4 | 0.1301 | 0.0073571 | 12.7% | 34.38% | 55.76% | 62.44%
| N12 - L37 | 9.919 | 0 | 5.995 | 0.397 | 0.258 | 13.378 | 1.8 | 0.0042469 | 0.22021 | 16.69% | 28.1% | 73.4% | 25.16% | 1.8 | 0.0031852 | 0.16516 | 14.56% | 26.57% | 55.05% | 30.16% | 1.4 | 0.0026327 | 0.13651 | 12.04% | 36.98% | 58.5% | 60.32%
| N12 - L38 | 15.563 | 0 | 1.968 | 4.334 | 10.515 | 3.235 | 1.8 | 0.17309 | 0.053251 | 12.25% | 20.04% | 57.7% | 26.42% | 1.8 | 0.12981 | 0.039938 | 11.54% | 20.37% | 43.27% | 31.43% | 1.4 | 0.1073 | 0.03301 | 9.536% | 27.96% | 45.98% | 62.34%
| N12 - L39 | 10.391 | 0 | 5.888 | 0.368 | 0.233 | 13.762 | 1.8 | 0.0038354 | 0.22653 | 16.28% | 28.39% | 75.51% | 25.52% | 1.8 | 0.0028765 | 0.1699 | 14.3% | 26.95% | 56.63% | 30.47% | 1.4 | 0.0023776 | 0.14043 | 11.82% | 37.23% | 60.18% | 60.92%
| N12 - L40 | 16.035 | 0 | 1.861 | 4.305 | 10.49 | 3.619 | 1.8 | 0.17267 | 0.059572 | 11.99% | 19.85% | 57.56% | 26.73% | 1.8 | 0.12951 | 0.044679 | 11.37% | 20.29% | 43.17% | 31.71% | 1.4 | 0.10704 | 0.036929 | 9.396% | 27.84% | 45.87% | 62.88%
| N12 - L41 | 10.358 | 0 | 0.83 | 1.026 | 3.449 | 9.386 | 1.8 | 0.056774 | 0.1545 | 3.644% | 15.64% | 51.5% | 24.49% | 1.8 | 0.04258 | 0.11588 | 3.199% | 14.01% | 38.63% | 29.68% | 1.4 | 0.035194 | 0.095776 | 2.644% | 16.1% | 41.05% | 59.19%
| N12 - L42 | 16.065 | 0 | 3.19 | 4.833 | 13.982 | 0.699 | 1.8 | 0.23016 | 0.011506 | 14.8% | 25.47% | 76.72% | 27.47% | 1.8 | 0.17262 | 0.0086296 | 14.04% | 25.81% | 57.54% | 32.24% | 1.4 | 0.14267 | 0.0071327 | 11.6% | 34.47% | 61.15% | 64.04%
| N12 - L43 | 9.987 | 0 | 5.917 | 0.403 | 0.276 | 13.212 | 1.8 | 0.0045432 | 0.21748 | 16.46% | 27.72% | 72.49% | 25.09% | 1.8 | 0.0034074 | 0.16311 | 14.37% | 26.24% | 54.37% | 30.1% | 1.4 | 0.0028163 | 0.13482 | 11.88% | 36.51% | 57.78% | 60.18%
| N12 - L44 | 15.694 | 0 | 1.897 | 4.209 | 10.809 | 3.127 | 1.8 | 0.17793 | 0.051473 | 11.86% | 20.3% | 59.31% | 26.58% | 1.8 | 0.13344 | 0.038605 | 11.19% | 20.6% | 44.48% | 31.56% | 1.4 | 0.1103 | 0.031908 | 9.249% | 28.03% | 47.27% | 62.61%
| N12 - L45 | 10.446 | 0 | 5.806 | 0.364 | 0.228 | 13.568 | 1.8 | 0.0037531 | 0.22334 | 16.04% | 27.97% | 74.45% | 25.41% | 1.8 | 0.0028148 | 0.16751 | 14.1% | 26.58% | 55.84% | 30.38% | 1.4 | 0.0023265 | 0.13845 | 11.65% | 36.71% | 59.34% | 60.73%
| N12 - L46 | 16.153 | 0 | 1.786 | 4.171 | 10.761 | 3.482 | 1.8 | 0.17714 | 0.057317 | 11.58% | 20.07% | 59.05% | 26.86% | 1.8 | 0.13285 | 0.042988 | 11% | 20.48% | 44.28% | 31.82% | 1.4 | 0.10981 | 0.035531 | 9.09% | 27.85% | 47.06% | 63.09%
| N12 - L47 | 9.703 | 0 | 0.822 | 1.114 | 0.98 | 9.385 | 1.8 | 0.016132 | 0.15449 | 3.858% | 15.77% | 51.5% | 23.2% | 1.8 | 0.012099 | 0.11586 | 3.356% | 14% | 38.62% | 28.5% | 1.4 | 0.01 | 0.095765 | 2.774% | 16.08% | 41.04% | 56.77%
| N12 - L48 | 15.41 | 0 | 3.198 | 2.692 | 9.554 | 0.7 | 1.8 | 0.15727 | 0.011523 | 10.78% | 16.88% | 52.42% | 24.61% | 1.8 | 0.11795 | 0.008642 | 10.13% | 16.8% | 39.32% | 29.83% | 1.4 | 0.09749 | 0.0071429 | 8.374% | 21.78% | 41.78% | 58.97%
| N12 - L49 | 9.973 | 0 | 5.923 | 0.388 | 0.243 | 13.207 | 1.8 | 0.004 | 0.2174 | 16.48% | 27.73% | 72.47% | 25.07% | 1.8 | 0.003 | 0.16305 | 14.39% | 26.24% | 54.35% | 30.08% | 1.4 | 0.0024796 | 0.13477 | 11.89% | 36.52% | 57.76% | 60.14%
| N12 - L50 | 15.68 | 0 | 1.903 | 4.195 | 10.777 | 3.122 | 1.8 | 0.1774 | 0.051391 | 11.83% | 20.24% | 59.13% | 26.55% | 1.8 | 0.13305 | 0.038543 | 11.17% | 20.54% | 44.35% | 31.54% | 1.4 | 0.10997 | 0.031857 | 9.228% | 27.94% | 47.13% | 62.56%
| N12 - L51 | 10.444 | 0 | 5.82 | 0.367 | 0.234 | 13.596 | 1.8 | 0.0038519 | 0.2238 | 16.08% | 28.03% | 74.6% | 25.43% | 1.8 | 0.0028889 | 0.16785 | 14.13% | 26.63% | 55.95% | 30.4% | 1.4 | 0.0023878 | 0.13873 | 11.68% | 36.79% | 59.46% | 60.76%
| N12 - L52 | 16.151 | 0 | 1.8 | 4.174 | 10.768 | 3.51 | 1.8 | 0.17725 | 0.057778 | 11.6% | 20.08% | 59.08% | 26.88% | 1.8 | 0.13294 | 0.043333 | 11.02% | 20.5% | 44.31% | 31.83% | 1.4 | 0.10988 | 0.035816 | 9.106% | 27.87% | 47.09% | 63.13%
| N12 - L53 | 16.986 | 0 | 5.672 | 0.575 | 0.395 | 15.147 | 1.8 | 0.0065021 | 0.24933 | 14.4% | 27.73% | 83.11% | 28.38% | 1.8 | 0.0048765 | 0.187 | 13.82% | 28.56% | 62.33% | 32.99% | 1.4 | 0.0040306 | 0.15456 | 11.42% | 38.62% | 66.24% | 65.54%
| N12 - L54 | 25.616 | 0 | 0.304 | 6.143 | 15.874 | 0.191 | 1.8 | 0.2613 | 0.003144 | 13.98% | 26.35% | 87.1% | 31.32% | 1.8 | 0.19598 | 0.002358 | 14.91% | 30.2% | 65.33% | 35.59% | 1.4 | 0.16198 | 0.001949 | 12.32% | 41.05% | 69.42% | 70.08%
| N12 - L55 | 13.664 | 0 | 4.74 | 1.6 | 6.48 | 12.296 | 1.8 | 0.10667 | 0.2024 | 13.2% | 23.67% | 67.47% | 28.81% | 1.8 | 0.08 | 0.1518 | 12.13% | 23.37% | 50.6% | 33.42% | 1.4 | 0.066122 | 0.12547 | 10.02% | 31.74% | 53.77% | 66.8%
| N12 - L56 | 20.222 | 0 | 0.136 | 5.949 | 18.518 | 0.702 | 1.8 | 0.30482 | 0.011556 | 14.43% | 31.53% | 101.6% | 32.22% | 1.8 | 0.22862 | 0.0086667 | 14.42% | 33.56% | 76.21% | 36.09% | 1.4 | 0.18896 | 0.0071633 | 11.92% | 44.34% | 80.98% | 71.8%
400kV CT Structure x 2400mm high | MAX | 49.64 |  | 6.44 | 10.91 | 71.48 | 30.03 | 2.7 |  | Worst Load Case = | 12.47% | 34.36% | 116.2% | 32.78% | 2.7 |  | Worst Load Case = | 11.75% | 33.49% | 87.16% | 36.23% | 2.2 |  | Worst Load Case = | 8.851% | 35.05% | 80.56% | 68.12%
| 1 | 33.38 | 0 | 0 | 10.39 | 68.08 | 0 | 2.7 | 0.49807 | 0 | 11.99% | 33.05% | 110.7% | 31.58% | 2.7 | 0.37355 | 0 | 11.19% | 31.89% | 83.01% | 35.33% | 2.2 | 0.28132 | 0 | 8.429% | 33.38% | 76.72% | 66.64%
| 2 | 33.38 | 0 | 4.41 | 4.65 | 36.8 | 20.7 | 2.7 | 0.26923 | 0.15144 | 7.398% | 17.55% | 59.83% | 28.04% | 2.7 | 0.20192 | 0.11358 | 6.904% | 16.85% | 44.87% | 32.81% | 2.2 | 0.15207 | 0.085537 | 5.199% | 17.32% | 41.47% | 62.41%
| 3 | 35.46 | 0 | 0 | 6.43 | 35.96 | 0 | 2.7 | 0.26308 | 0 | 7.333% | 17.55% | 58.46% | 24.99% | 2.7 | 0.19731 | 0 | 6.927% | 17.23% | 43.85% | 30.15% | 2.2 | 0.1486 | 0 | 5.217% | 18.34% | 40.53% | 57.68%
| 4 | 35.46 | 0 | 4.6 | 0 | 0 | 21.45 | 2.7 | 0 | 0.15693 | 5.246% | 10.71% | 34.87% | 22.76% | 2.7 | 0 | 0.1177 | 4.955% | 10.59% | 26.15% | 28.2% | 2.2 | 0 | 0.088636 | 3.732% | 11.51% | 24.17% | 54.26%
| 5 | 35.05 | 0 | 0 | 10.91 | 71.48 | 0 | 2.7 | 0.52294 | 0 | 12.47% | 34.36% | 116.2% | 32.78% | 2.7 | 0.39221 | 0 | 11.75% | 33.49% | 87.16% | 36.23% | 2.2 | 0.29537 | 0 | 8.851% | 35.05% | 80.56% | 68.12%
| 6 | 35.05 | 0 | 4.63 | 4.88 | 38.64 | 21.73 | 2.7 | 0.28269 | 0.15898 | 7.69% | 18.24% | 62.82% | 28.79% | 2.7 | 0.21202 | 0.11923 | 7.247% | 17.69% | 47.11% | 33.45% | 2.2 | 0.15967 | 0.089793 | 5.457% | 18.18% | 43.55% | 63.47%
| 7 | 49.64 | 0 | 0 | 9 | 50.34 | 0 | 2.7 | 0.36829 | 0 | 9.483% | 22.7% | 81.84% | 29.45% | 2.7 | 0.27621 | 0 | 9.695% | 24.12% | 61.38% | 34% | 2.2 | 0.20802 | 0 | 7.301% | 25.67% | 56.73% | 63.93%
| 8 | 49.64 | 0 | 6.44 | 0 | 0 | 30.03 | 2.7 | 0 | 0.2197 | 6.786% | 13.86% | 48.82% | 25.58% | 2.7 | 0 | 0.16477 | 6.937% | 14.82% | 36.62% | 30.8% | 2.2 | 0 | 0.12409 | 5.225% | 16.12% | 33.84% | 58.43%
400kV CVT Structure x 2400mm high | MAX | 12.42 |  | 4.51 | 3.55 | 13.94 | 25.27 | 2 |  | Worst Load Case = | 10.61% | 34.33% | 101.1% | 27.58% | 1.9 |  | Worst Load Case = | 9.811% | 34.73% | 88.42% | 34.12% | 1.5 |  | Worst Load Case = | 7.871% | 40.64% | 89.85% | 67.82%
| 1 | 8.06 | 0 | 2.1 | 2.34 | 9.13 | 15.94 | 2 | 0.12173 | 0.21253 | 7.432% | 21.09% | 63.76% | 26.34% | 1.9 | 0.10116 | 0.17662 | 6.84% | 21.04% | 55.77% | 32.98% | 1.5 | 0.081156 | 0.14169 | 5.487% | 23.87% | 56.68% | 65.52%
| 2 | 8.06 | 0 | 4.29 | 0 | 0 | 24.06 | 2 | 0 | 0.3208 | 10.14% | 32.84% | 96.24% | 26.82% | 1.9 | 0 | 0.26659 | 9.332% | 33.07% | 84.19% | 33.35% | 1.5 | 0 | 0.21387 | 7.487% | 38.68% | 85.55% | 66.29%
| 3 | 8.87 | 0 | 0.58 | 2.54 | 9.96 | 4.41 | 2 | 0.1328 | 0.0588 | 6.099% | 14.15% | 39.84% | 22.49% | 1.9 | 0.11036 | 0.048864 | 5.668% | 14.58% | 34.85% | 28.79% | 1.5 | 0.088533 | 0.0392 | 4.547% | 17.83% | 35.41% | 56.98%
| 4 | 8.87 | 0 | 2.79 | 0 | 0 | 11.93 | 2 | 0 | 0.15907 | 6.531% | 16.72% | 47.72% | 21.82% | 1.9 | 0 | 0.13219 | 6.069% | 17.17% | 41.74% | 28.04% | 1.5 | 0 | 0.10604 | 4.869% | 20.75% | 42.42% | 55.47%
| 5 | 8.47 | 0 | 2.21 | 2.45 | 9.59 | 16.74 | 2 | 0.12787 | 0.2232 | 7.761% | 22.04% | 66.96% | 26.99% | 1.9 | 0.10626 | 0.18548 | 7.178% | 22.1% | 58.57% | 33.67% | 1.5 | 0.085244 | 0.1488 | 5.758% | 25.08% | 59.52% | 66.87%
| 6 | 8.47 | 0 | 4.51 | 0 | 0 | 25.27 | 2 | 0 | 0.33693 | 10.61% | 34.33% | 101.1% | 27.58% | 1.9 | 0 | 0.28 | 9.811% | 34.73% | 88.42% | 34.12% | 1.5 | 0 | 0.22462 | 7.871% | 40.64% | 89.85% | 67.82%
| 7 | 12.42 | 0 | 0.81 | 3.55 | 13.94 | 6.18 | 2 | 0.18587 | 0.0824 | 8.178% | 18.99% | 55.76% | 25.36% | 1.9 | 0.15446 | 0.068476 | 7.921% | 20.4% | 48.78% | 31.91% | 1.5 | 0.12391 | 0.054933 | 6.354% | 24.94% | 49.56% | 62.92%
| 8 | 12.42 | 0 | 3.9 | 0 | 0 | 16.7 | 2 | 0 | 0.22267 | 8.759% | 22.45% | 66.8% | 24.37% | 1.9 | 0 | 0.18504 | 8.484% | 24.03% | 58.43% | 30.79% | 1.5 | 0 | 0.14844 | 6.806% | 29.04% | 59.38% | 60.69%
400kV Cable Sealing End
400kV Circuit Breaker
Super Gride Transformer
132kV High Level - Post Insulator Structure x 6700mm high
132kV Low Level - Post Insulator Structure x 2400mm high
132kV High Level - Surge Arrester Structure x 6000mm high | MAX | 4.51 |  | 3.29 | 2.57 | 7.66 | 14.38 | 1.7 |  | Worst Load Case = | 11.24% | 34.76% | 93.66% | 26.21% | 1.6 |  | Worst Load Case = | 10.09% | 34.45% | 84.26% | 33.22% | 1.3 |  | Worst Load Case = | 7.644% | 38.05% | 78.54% | 64.02%
| 1 | 2.62 | 0 | 1.67 | 1.66 | 4.89 | 10.21 | 1.7 | 0.090242 | 0.18842 | 8.138% | 23.74% | 66.5% | 25.13% | 1.6 | 0.076406 | 0.15953 | 7.223% | 23.2% | 59.82% | 32.01% | 1.3 | 0.05787 | 0.12083 | 5.471% | 24.67% | 55.77% | 62.07%
| 2 | 2.62 | 0 | 3.1 | 0 | 0 | 13.7 | 1.7 | 0 | 0.25283 | 10.71% | 33.19% | 89.23% | 24.88% | 1.6 | 0 | 0.21406 | 9.51% | 32.81% | 80.27% | 31.65% | 1.3 | 0 | 0.16213 | 7.203% | 36.23% | 74.83% | 61.33%
| 3 | 3.22 | 0 | 0.97 | 1.84 | 5.47 | 5.92 | 1.7 | 0.10095 | 0.10925 | 7.114% | 14.04% | 38.56% | 22.94% | 1.6 | 0.085469 | 0.0925 | 6.381% | 14.28% | 34.69% | 29.55% | 1.3 | 0.064734 | 0.070059 | 4.833% | 16.66% | 32.34% | 57.6%
| 4 | 3.22 | 0 | 2.35 | 0 | 0 | 8.57 | 1.7 | 0 | 0.15815 | 8.037% | 21.17% | 55.82% | 21.65% | 1.6 | 0 | 0.13391 | 7.209% | 21.33% | 50.21% | 28.03% | 1.3 | 0 | 0.10142 | 5.46% | 24.16% | 46.81% | 54.82%
| 5 | 2.75 | 0 | 1.76 | 1.74 | 5.13 | 10.72 | 1.7 | 0.094671 | 0.19783 | 8.534% | 24.88% | 69.82% | 25.68% | 1.6 | 0.080156 | 0.1675 | 7.592% | 24.37% | 62.81% | 32.63% | 1.3 | 0.06071 | 0.12686 | 5.75% | 25.93% | 58.55% | 63.16%
| 6 | 2.75 | 0 | 3.26 | 0 | 0 | 14.38 | 1.7 | 0 | 0.26537 | 11.24% | 34.76% | 93.66% | 25.46% | 1.6 | 0 | 0.22469 | 10% | 34.45% | 84.26% | 32.28% | 1.3 | 0 | 0.17018 | 7.574% | 38.05% | 78.54% | 62.43%
| 7 | 4.51 | 0 | 1.36 | 2.57 | 7.66 | 8.29 | 1.7 | 0.14136 | 0.15299 | 9.725% | 19.22% | 54% | 26.21% | 1.6 | 0.11969 | 0.12953 | 8.92% | 19.98% | 48.57% | 33.22% | 1.3 | 0.090651 | 0.098107 | 6.756% | 23.3% | 45.28% | 64.02%
| 8 | 4.51 | 0 | 3.29 | 0 | 0 | 12 | 1.7 | 0 | 0.22145 | 11% | 29% | 78.16% | 24.23% | 1.6 | 0 | 0.1875 | 10.09% | 29.86% | 70.31% | 30.92% | 1.3 | 0 | 0.14201 | 7.644% | 33.83% | 65.54% | 59.86%
132kV Low Level - Surge Arrester Structure x 2400mm high | MAX | 2.56 |  | 2.58 | 1.64 | 3.9 | 9.5 | 1.5 |  | Worst Load Case = | 11.58% | 34.87% | 90.07% | 25.33% | 1.4 |  | Worst Load Case = | 10.34% | 35.22% | 83.09% | 32.56% | 1.1 |  | Worst Load Case = | 8.372% | 44.06% | 85.65% | 65.62%
| 1 | 1.47 | 0 | 1.67 | 1.03 | 2.44 | 7.7 | 1.5 | 0.057837 | 0.18252 | 8.824% | 27.34% | 73.01% | 24.79% | 1.4 | 0.049796 | 0.15714 | 7.862% | 27.32% | 67.35% | 31.93% | 1.1 | 0.040331 | 0.12727 | 6.367% | 33.18% | 69.42% | 64.32%
| 2 | 1.47 | 0 | 2.45 | 0 | 0 | 9.04 | 1.5 | 0 | 0.21428 | 11.02% | 33.22% | 85.71% | 24.23% | 1.4 | 0 | 0.18449 | 9.816% | 33.5% | 79.07% | 31.23% | 1.1 | 0 | 0.14942 | 7.951% | 41.89% | 81.5% | 62.9%
| 3 | 1.83 | 0 | 0.97 | 1.17 | 2.78 | 4.47 | 1.5 | 0.065896 | 0.10596 | 6.779% | 15.74% | 42.38% | 22.24% | 1.4 | 0.056735 | 0.091224 | 6.089% | 15.86% | 39.1% | 28.93% | 1.1 | 0.04595 | 0.073884 | 4.932% | 19.26% | 40.3% | 57.99%
| 4 | 1.83 | 0 | 1.66 | 0 | 0 | 5.09 | 1.5 | 0 | 0.12065 | 7.404% | 19.19% | 48.26% | 20.76% | 1.4 | 0 | 0.10388 | 6.651% | 19.68% | 44.52% | 27.15% | 1.1 | 0 | 0.084132 | 5.387% | 25.27% | 45.89% | 54.32%
| 5 | 1.54 | 0 | 1.76 | 1.08 | 2.56 | 8.09 | 1.5 | 0.060681 | 0.19176 | 9.271% | 28.69% | 76.71% | 25.33% | 1.4 | 0.052245 | 0.1651 | 8.274% | 28.72% | 70.76% | 32.56% | 1.1 | 0.042314 | 0.13372 | 6.701% | 34.89% | 72.94% | 65.62%
| 6 | 1.54 | 0 | 2.58 | 0 | 0 | 9.5 | 1.5 | 0 | 0.22519 | 11.58% | 34.87% | 90.07% | 24.77% | 1.4 | 0 | 0.19388 | 10.34% | 35.22% | 83.09% | 31.84% | 1.1 | 0 | 0.15702 | 8.372% | 44.06% | 85.65% | 64.17%
| 7 | 2.56 | 0 | 1.36 | 1.64 | 3.9 | 6.25 | 1.5 | 0.092444 | 0.14815 | 9.348% | 21.66% | 59.26% | 25.06% | 1.4 | 0.079592 | 0.12755 | 8.536% | 22.19% | 54.66% | 32.24% | 1.1 | 0.064463 | 0.10331 | 6.914% | 26.96% | 56.35% | 64.73%
| 8 | 2.56 | 0 | 2.32 | 0 | 0 | 7.12 | 1.5 | 0 | 0.16877 | 10.18% | 26.4% | 67.51% | 22.75% | 1.4 | 0 | 0.14531 | 9.296% | 27.52% | 62.27% | 29.49% | 1.1 | 0 | 0.11769 | 7.529% | 35.34% | 64.19% | 59.04%
132kV Disconnector with 2 Earth Switches Structure x 2600mm high
132kV Earth Switch Structure x 2600mm high | MAX | 9.601 |  | 4.169 | 3.202 | 10.031 | 4.589 | 1.6 |  | Worst Load Case = | 15.11% | 31.37% | 78.37% | 25.65% | 1.4 |  | Worst Load Case = | 16.75% | 37.29% | 87.73% | 35.73% | 1.1 |  | Worst Load Case = | 13.57% | 46.72% | 90.44% | 71.18%
| N4 - L1 | 2.325 | 0 | 2.255 | 0 | 0 | 2.74 | 1.6 | 0 | 0.057083 | 8.797% | 11.01% | 21.41% | 18.82% | 1.4 | 0 | 0.055918 | 9.035% | 14.56% | 23.97% | 25.31% | 1.1 | 0 | 0.045289 | 7.318% | 21.79% | 24.7% | 50.43%
| N4 - L2 | 0.115 | 0 | 0.518 | 1.474 | 3.717 | 0.756 | 1.6 | 0.077437 | 0.01575 | 6.375% | 12.53% | 29.04% | 19.09% | 1.4 | 0.075857 | 0.015429 | 6.26% | 15.13% | 32.51% | 25.85% | 1.1 | 0.061438 | 0.012496 | 5.07% | 20.03% | 33.51% | 51.91%
| N4 - L3 | 0.86 | 0 | 2.676 | 0 | 0 | 3.118 | 1.6 | 0 | 0.064958 | 10.75% | 13.11% | 24.36% | 18.61% | 1.4 | 0 | 0.063633 | 10.72% | 16.89% | 27.27% | 25.07% | 1.1 | 0 | 0.051537 | 8.684% | 25.45% | 28.11% | 50.18%
| N4 - L4 | 1.35 | 0 | 0.94 | 1.474 | 3.717 | 1.134 | 1.6 | 0.077437 | 0.023625 | 6.955% | 12.22% | 29.04% | 19.65% | 1.4 | 0.075857 | 0.023143 | 7.005% | 15.13% | 32.51% | 26.63% | 1.1 | 0.061438 | 0.018744 | 5.673% | 20.03% | 33.51% | 53.31%
| N4 - L5 | 0.651 | 0 | 2.489 | 0 | 0 | 2.981 | 1.6 | 0 | 0.062104 | 10.04% | 12.46% | 23.29% | 18.48% | 1.4 | 0 | 0.060837 | 9.973% | 15.95% | 26.07% | 24.88% | 1.1 | 0 | 0.049273 | 8.077% | 23.92% | 26.88% | 49.82%
| N4 - L6 | 2.861 | 0 | 0.752 | 1.474 | 3.717 | 0.997 | 1.6 | 0.077437 | 0.020771 | 6.387% | 11.85% | 29.04% | 20.03% | 1.4 | 0.075857 | 0.020347 | 6.63% | 15.13% | 32.51% | 27.11% | 1.1 | 0.061438 | 0.016479 | 5.37% | 20.03% | 33.51% | 54.05%
| N4 - L7 | 2.111 | 0 | 2.2 | 0.456 | 2.353 | 2.665 | 1.6 | 0.049021 | 0.055521 | 8.803% | 10.76% | 20.82% | 19.95% | 1.4 | 0.04802 | 0.054388 | 9.002% | 14.18% | 23.31% | 27.03% | 1.1 | 0.038893 | 0.04405 | 7.291% | 21.23% | 24.03% | 54%
| N4 - L8 | 0.044 | 0 | 0.49 | 2.05 | 6.63 | 0.716 | 1.6 | 0.13812 | 0.014917 | 8.613% | 21.25% | 51.8% | 20.8% | 1.4 | 0.13531 | 0.014612 | 8.445% | 25.31% | 57.99% | 28.5% | 1.1 | 0.10959 | 0.011835 | 6.84% | 32.25% | 59.77% | 57.46%
| N4 - L9 | 0.715 | 0 | 2.602 | 0.266 | 0.802 | 3.025 | 1.6 | 0.016708 | 0.063021 | 10.54% | 12.77% | 23.63% | 18.92% | 1.4 | 0.016367 | 0.061735 | 10.48% | 16.41% | 26.46% | 25.54% | 1.1 | 0.013256 | 0.05 | 8.488% | 24.73% | 27.27% | 51.17%
| N4 - L10 | 1.44 | 0 | 0.892 | 1.861 | 5.08 | 1.076 | 1.6 | 0.10583 | 0.022417 | 8.195% | 16.37% | 39.69% | 20.45% | 1.4 | 0.10367 | 0.021959 | 8.269% | 20.24% | 44.43% | 27.86% | 1.1 | 0.083967 | 0.017785 | 6.697% | 26.45% | 45.8% | 55.85%
| N4 - L11 | 0.726 | 0 | 2.423 | 0.133 | 0.395 | 2.895 | 1.6 | 0.0082292 | 0.060312 | 9.778% | 12.09% | 22.62% | 18.65% | 1.4 | 0.0080612 | 0.059082 | 9.723% | 15.5% | 25.32% | 25.13% | 1.1 | 0.0065289 | 0.047851 | 7.875% | 23.26% | 26.1% | 50.32%
| N4 - L12 | 2.88 | 0 | 0.713 | 1.461 | 3.882 | 0.946 | 1.6 | 0.080875 | 0.019708 | 6.273% | 12.23% | 30.33% | 20.1% | 1.4 | 0.079224 | 0.019306 | 6.514% | 15.58% | 33.95% | 27.23% | 1.1 | 0.064165 | 0.015636 | 5.276% | 20.45% | 35% | 54.28%
| N4 - L13 | 1.901 | 0 | 2.155 | 0.912 | 4.706 | 2.602 | 1.6 | 0.098042 | 0.054208 | 9.207% | 13.5% | 36.77% | 21.23% | 1.4 | 0.096041 | 0.053102 | 9.376% | 16.38% | 41.16% | 29.03% | 1.1 | 0.077785 | 0.043008 | 7.594% | 20.77% | 42.43% | 58.18%
| N4 - L14 | 0.202 | 0 | 0.462 | 2.627 | 9.553 | 0.676 | 1.6 | 0.19902 | 0.014083 | 10.86% | 29.88% | 74.63% | 22.94% | 1.4 | 0.19496 | 0.013796 | 10.69% | 35.51% | 83.55% | 31.91% | 1.1 | 0.1579 | 0.011174 | 8.656% | 44.5% | 86.13% | 64.59%
| N4 - L15 | 0.574 | 0 | 2.536 | 0.533 | 1.605 | 2.945 | 1.6 | 0.033437 | 0.061354 | 10.47% | 12.47% | 23.01% | 19.24% | 1.4 | 0.032755 | 0.060102 | 10.38% | 15.98% | 25.76% | 26.05% | 1.1 | 0.026529 | 0.048678 | 8.409% | 24.09% | 26.55% | 52.24%
| N4 - L16 | 1.53 | 0 | 0.844 | 2.247 | 6.452 | 1.018 | 1.6 | 0.13442 | 0.021208 | 9.514% | 20.54% | 50.41% | 21.33% | 1.4 | 0.13167 | 0.020776 | 9.617% | 25.36% | 56.43% | 29.22% | 1.1 | 0.10664 | 0.016826 | 7.789% | 32.9% | 58.17% | 58.66%
| N4 - L17 | 0.796 | 0 | 2.367 | 0.265 | 0.791 | 2.821 | 1.6 | 0.016479 | 0.058771 | 9.583% | 11.77% | 22.04% | 18.82% | 1.4 | 0.016143 | 0.057571 | 9.543% | 15.13% | 24.67% | 25.4% | 1.1 | 0.013074 | 0.046628 | 7.729% | 22.7% | 25.43% | 50.86%
| N4 - L18 | 2.899 | 0 | 0.674 | 1.449 | 4.057 | 0.895 | 1.6 | 0.084521 | 0.018646 | 6.164% | 12.63% | 31.7% | 20.18% | 1.4 | 0.082796 | 0.018265 | 6.403% | 16.05% | 35.48% | 27.35% | 1.1 | 0.067058 | 0.014793 | 5.186% | 20.9% | 36.58% | 54.53%
| N4 - L19 | 1.901 | 0 | 2.155 | 0 | 0 | 2.602 | 1.6 | 0 | 0.054208 | 8.479% | 10.57% | 20.33% | 18.63% | 1.4 | 0 | 0.053102 | 8.634% | 13.87% | 22.76% | 25.05% | 1.1 | 0 | 0.043008 | 6.993% | 20.77% | 23.46% | 49.95%
| N4 - L20 | 0.202 | 0 | 0.462 | 1.714 | 4.847 | 0.676 | 1.6 | 0.10098 | 0.014083 | 7.23% | 15.9% | 37.87% | 19.72% | 1.4 | 0.098918 | 0.013796 | 7.113% | 19.13% | 42.39% | 26.81% | 1.1 | 0.080116 | 0.011174 | 5.761% | 24.87% | 43.7% | 53.9%
| N4 - L21 | 0.574 | 0 | 2.537 | 0 | 0 | 2.945 | 1.6 | 0 | 0.061354 | 10.25% | 12.48% | 23.01% | 18.44% | 1.4 | 0 | 0.060102 | 10.17% | 15.98% | 25.76% | 24.83% | 1.1 | 0 | 0.048678 | 8.233% | 24.1% | 26.55% | 49.72%
| N4 - L22 | 1.53 | 0 | 0.844 | 1.714 | 4.847 | 1.018 | 1.6 | 0.10098 | 0.021208 | 7.573% | 15.48% | 37.87% | 20.31% | 1.4 | 0.098918 | 0.020776 | 7.655% | 19.13% | 42.39% | 27.63% | 1.1 | 0.080116 | 0.016826 | 6.2% | 24.87% | 43.7% | 55.35%
| N4 - L23 | 0.796 | 0 | 2.367 | 0 | 0 | 2.821 | 1.6 | 0 | 0.058771 | 9.524% | 11.77% | 22.04% | 18.44% | 1.4 | 0 | 0.057571 | 9.484% | 15.13% | 24.67% | 24.81% | 1.1 | 0 | 0.046628 | 7.681% | 22.7% | 25.43% | 49.65%
| N4 - L24 | 2.899 | 0 | 0.674 | 1.714 | 4.847 | 0.895 | 1.6 | 0.10098 | 0.018646 | 7.104% | 15.06% | 37.87% | 20.66% | 1.4 | 0.098918 | 0.018265 | 7.379% | 19.13% | 42.39% | 28.08% | 1.1 | 0.080116 | 0.014793 | 5.977% | 24.87% | 43.7% | 56.05%
| N4 - L25 | 1.213 | 0 | 2.01 | 0 | 0 | 2.324 | 1.6 | 0 | 0.048417 | 8.019% | 9.732% | 18.16% | 18.3% | 1.4 | 0 | 0.047429 | 8.053% | 12.64% | 20.33% | 24.58% | 1.1 | 0 | 0.038413 | 6.523% | 19.07% | 20.95% | 49.1%
| N4 - L26 | 4.077 | 0 | 0.096 | 1.974 | 5.74 | 0.114 | 1.6 | 0.11958 | 0.002375 | 7.451% | 17.33% | 44.84% | 21.15% | 1.4 | 0.11714 | 0.0023265 | 7.919% | 22.49% | 50.2% | 28.78% | 1.1 | 0.094876 | 0.0018843 | 6.413% | 29.11% | 51.75% | 57.29%
| N4 - L27 | 0.988 | 0 | 2.535 | 0.131 | 0.894 | 3.026 | 1.6 | 0.018625 | 0.063042 | 10.17% | 12.57% | 23.64% | 19.04% | 1.4 | 0.018245 | 0.061755 | 10.17% | 16.21% | 26.47% | 25.72% | 1.1 | 0.014777 | 0.050017 | 8.237% | 24.33% | 27.28% | 51.48%
| N4 - L28 | 1.222 | 0 | 0.799 | 1.845 | 5.741 | 1.043 | 1.6 | 0.1196 | 0.021729 | 8.019% | 18.09% | 44.85% | 20.78% | 1.4 | 0.11716 | 0.021286 | 8.056% | 22.12% | 50.21% | 28.39% | 1.1 | 0.094893 | 0.01724 | 6.525% | 28.34% | 51.76% | 56.98%
| N4 - L29 | 2.441 | 0 | 2.368 | 0 | 0 | 2.877 | 1.6 | 0 | 0.059937 | 9.217% | 11.53% | 22.48% | 18.93% | 1.4 | 0 | 0.058714 | 9.488% | 15.29% | 25.16% | 25.47% | 1.1 | 0 | 0.047554 | 7.684% | 22.88% | 25.94% | 50.73%
| N4 - L30 | 0.121 | 0 | 0.544 | 1.548 | 3.903 | 0.793 | 1.6 | 0.081312 | 0.016521 | 6.694% | 13.15% | 30.49% | 19.22% | 1.4 | 0.079653 | 0.016184 | 6.574% | 15.89% | 34.14% | 26.04% | 1.1 | 0.064512 | 0.013107 | 5.325% | 21.03% | 35.19% | 52.3%
| N4 - L31 | 0.903 | 0 | 2.81 | 0 | 0 | 3.274 | 1.6 | 0 | 0.068208 | 11.28% | 13.76% | 25.58% | 18.7% | 1.4 | 0 | 0.066816 | 11.26% | 17.74% | 28.64% | 25.21% | 1.1 | 0 | 0.054116 | 9.119% | 26.73% | 29.52% | 50.46%
| N4 - L32 | 1.417 | 0 | 0.987 | 1.548 | 3.903 | 1.19 | 1.6 | 0.081312 | 0.024792 | 7.294% | 12.81% | 30.49% | 19.81% | 1.4 | 0.079653 | 0.024286 | 7.356% | 15.89% | 34.14% | 26.86% | 1.1 | 0.064512 | 0.019669 | 5.958% | 21.03% | 35.19% | 53.79%
| N4 - L33 | 0.684 | 0 | 2.613 | 0 | 0 | 3.13 | 1.6 | 0 | 0.065208 | 10.54% | 13.07% | 24.45% | 18.57% | 1.4 | 0 | 0.063878 | 10.47% | 16.74% | 27.38% | 25.02% | 1.1 | 0 | 0.051736 | 8.479% | 25.11% | 28.22% | 50.09%
| N4 - L34 | 3.004 | 0 | 0.79 | 1.548 | 3.903 | 1.047 | 1.6 | 0.081312 | 0.021812 | 6.69% | 12.41% | 30.49% | 20.21% | 1.4 | 0.079653 | 0.021367 | 6.963% | 15.89% | 34.14% | 27.38% | 1.1 | 0.064512 | 0.017306 | 5.64% | 21.03% | 35.19% | 54.57%
| N4 - L35 | 2.216 | 0 | 2.31 | 0.479 | 2.47 | 2.798 | 1.6 | 0.051458 | 0.058292 | 9.223% | 11.28% | 21.86% | 20.12% | 1.4 | 0.050408 | 0.057102 | 9.452% | 14.89% | 24.47% | 27.28% | 1.1 | 0.040826 | 0.046248 | 7.656% | 22.29% | 25.23% | 54.51%
| N4 - L36 | 0.046 | 0 | 0.515 | 2.153 | 6.962 | 0.751 | 1.6 | 0.14504 | 0.015646 | 9.046% | 22.31% | 54.39% | 21.04% | 1.4 | 0.14208 | 0.015327 | 8.87% | 26.57% | 60.89% | 28.88% | 1.1 | 0.11507 | 0.012413 | 7.184% | 33.86% | 62.77% | 58.25%
| N4 - L37 | 0.75 | 0 | 2.732 | 0.28 | 0.843 | 3.176 | 1.6 | 0.017562 | 0.066167 | 11.06% | 13.4% | 24.81% | 19.03% | 1.4 | 0.017204 | 0.064816 | 11% | 17.22% | 27.78% | 25.71% | 1.1 | 0.013934 | 0.052496 | 8.912% | 25.97% | 28.63% | 51.51%
| N4 - L38 | 1.512 | 0 | 0.936 | 1.954 | 5.334 | 1.13 | 1.6 | 0.11112 | 0.023542 | 8.591% | 17.17% | 41.67% | 20.66% | 1.4 | 0.10886 | 0.023061 | 8.681% | 21.25% | 46.65% | 28.18% | 1.1 | 0.088165 | 0.018678 | 7.031% | 27.77% | 48.09% | 56.5%
| N4 - L39 | 0.762 | 0 | 2.544 | 0.139 | 0.415 | 3.04 | 1.6 | 0.0086458 | 0.063333 | 10.26% | 12.68% | 23.75% | 18.74% | 1.4 | 0.0084694 | 0.062041 | 10.21% | 16.28% | 26.59% | 25.28% | 1.1 | 0.0068595 | 0.050248 | 8.268% | 24.43% | 27.41% | 50.62%
| N4 - L40 | 3.024 | 0 | 0.749 | 1.535 | 4.076 | 0.993 | 1.6 | 0.084917 | 0.020687 | 6.572% | 12.81% | 31.84% | 20.28% | 1.4 | 0.083184 | 0.020265 | 6.843% | 16.36% | 35.65% | 27.5% | 1.1 | 0.067372 | 0.016413 | 5.543% | 21.48% | 36.75% | 54.82%
| N4 - L41 | 1.996 | 0 | 2.262 | 0.958 | 4.941 | 2.732 | 1.6 | 0.10294 | 0.056917 | 9.646% | 14.15% | 38.6% | 21.49% | 1.4 | 0.10084 | 0.055755 | 9.842% | 17.2% | 43.22% | 29.42% | 1.1 | 0.081669 | 0.045157 | 7.972% | 21.81% | 44.55% | 58.98%
| N4 - L42 | 0.213 | 0 | 0.485 | 2.758 | 10.031 | 0.709 | 1.6 | 0.20898 | 0.014771 | 11.4% | 31.37% | 78.37% | 23.35% | 1.4 | 0.20471 | 0.014469 | 11.22% | 37.29% | 87.73% | 32.58% | 1.1 | 0.1658 | 0.011719 | 9.087% | 46.72% | 90.44% | 65.99%
| N4 - L43 | 0.602 | 0 | 2.663 | 0.56 | 1.685 | 3.092 | 1.6 | 0.035104 | 0.064417 | 10.99% | 13.09% | 24.16% | 19.37% | 1.4 | 0.034388 | 0.063102 | 10.9% | 16.78% | 27.04% | 26.24% | 1.1 | 0.027851 | 0.051107 | 8.831% | 25.3% | 27.88% | 52.64%
| N4 - L44 | 1.606 | 0 | 0.886 | 2.36 | 6.775 | 1.069 | 1.6 | 0.14115 | 0.022271 | 9.977% | 21.53% | 52.93% | 21.6% | 1.4 | 0.13827 | 0.021816 | 10.1% | 26.63% | 59.26% | 29.64% | 1.1 | 0.11198 | 0.017669 | 8.18% | 34.55% | 61.08% | 59.53%
| N4 - L45 | 0.836 | 0 | 2.485 | 0.279 | 0.83 | 2.962 | 1.6 | 0.017292 | 0.061708 | 10.05% | 12.35% | 23.14% | 18.93% | 1.4 | 0.016939 | 0.060449 | 10.02% | 15.88% | 25.91% | 25.56% | 1.1 | 0.013719 | 0.048959 | 8.115% | 23.84% | 26.7% | 51.18%
| N4 - L46 | 3.044 | 0 | 0.708 | 1.521 | 4.259 | 0.939 | 1.6 | 0.088729 | 0.019562 | 6.453% | 13.22% | 33.27% | 20.37% | 1.4 | 0.086918 | 0.019163 | 6.722% | 16.85% | 37.25% | 27.63% | 1.1 | 0.070397 | 0.015521 | 5.444% | 21.94% | 38.4% | 55.08%
| N4 - L47 | 1.996 | 0 | 2.262 | 0 | 0 | 2.733 | 1.6 | 0 | 0.056937 | 8.883% | 11.07% | 21.35% | 18.73% | 1.4 | 0 | 0.055776 | 9.063% | 14.56% | 23.9% | 25.19% | 1.1 | 0 | 0.045174 | 7.34% | 21.81% | 24.64% | 50.22%
| N4 - L48 | 0.213 | 0 | 0.485 | 1.8 | 5.09 | 0.709 | 1.6 | 0.10604 | 0.014771 | 7.591% | 16.7% | 39.77% | 19.88% | 1.4 | 0.10388 | 0.014469 | 7.469% | 20.09% | 44.52% | 27.07% | 1.1 | 0.084132 | 0.011719 | 6.05% | 26.12% | 45.89% | 54.42%
| N4 - L49 | 0.602 | 0 | 2.663 | 0 | 0 | 3.092 | 1.6 | 0 | 0.064417 | 10.76% | 13.09% | 24.16% | 18.52% | 1.4 | 0 | 0.063102 | 10.67% | 16.78% | 27.04% | 24.95% | 1.1 | 0 | 0.051107 | 8.642% | 25.3% | 27.88% | 49.98%
| N4 - L50 | 1.606 | 0 | 0.886 | 1.8 | 5.09 | 1.069 | 1.6 | 0.10604 | 0.022271 | 7.94% | 16.23% | 39.77% | 20.51% | 1.4 | 0.10388 | 0.021816 | 8.038% | 20.09% | 44.52% | 27.93% | 1.1 | 0.084132 | 0.017669 | 6.51% | 26.12% | 45.89% | 55.97%
| N4 - L51 | 0.836 | 0 | 2.485 | 0 | 0 | 2.962 | 1.6 | 0 | 0.061708 | 9.99% | 12.35% | 23.14% | 18.52% | 1.4 | 0 | 0.060449 | 9.957% | 15.88% | 25.91% | 24.94% | 1.1 | 0 | 0.048959 | 8.064% | 23.84% | 26.7% | 49.9%
| N4 - L52 | 3.044 | 0 | 0.708 | 1.8 | 5.09 | 0.939 | 1.6 | 0.10604 | 0.019562 | 7.44% | 15.77% | 39.77% | 20.88% | 1.4 | 0.10388 | 0.019163 | 7.75% | 20.09% | 44.52% | 28.41% | 1.1 | 0.084132 | 0.015521 | 6.277% | 26.12% | 45.89% | 56.71%
| N4 - L53 | 1.698 | 0 | 2.814 | 0 | 0 | 3.253 | 1.6 | 0 | 0.067771 | 11.12% | 13.49% | 25.41% | 18.92% | 1.4 | 0 | 0.066388 | 11.27% | 17.69% | 28.45% | 25.5% | 1.1 | 0 | 0.053769 | 9.132% | 26.69% | 29.33% | 50.91%
| N4 - L54 | 5.707 | 0 | 0.134 | 2.764 | 8.036 | 0.159 | 1.6 | 0.16742 | 0.0033125 | 10.12% | 23.53% | 62.78% | 23.32% | 1.4 | 0.164 | 0.0032449 | 11.09% | 31.49% | 70.29% | 32.07% | 1.1 | 0.13283 | 0.0026281 | 8.98% | 40.76% | 72.45% | 63.78%
| N4 - L55 | 1.185 | 0 | 3.042 | 0.157 | 1.073 | 3.632 | 1.6 | 0.022354 | 0.075667 | 12.16% | 15.03% | 28.38% | 19.52% | 1.4 | 0.021898 | 0.074122 | 12.2% | 19.46% | 31.77% | 26.44% | 1.1 | 0.017736 | 0.060033 | 9.885% | 29.2% | 32.75% | 52.95%
| N4 - L56 | 1.466 | 0 | 0.958 | 2.214 | 6.89 | 1.251 | 1.6 | 0.14354 | 0.026062 | 9.575% | 21.61% | 53.83% | 21.74% | 1.4 | 0.14061 | 0.025531 | 9.666% | 26.54% | 60.26% | 29.87% | 1.1 | 0.11388 | 0.020678 | 7.828% | 34.01% | 62.12% | 60.03%
| N5 - L1 | 8.237 | 0 | 3.591 | 0 | 0 | 3.932 | 1.6 | 0 | 0.081917 | 12.54% | 14.73% | 30.72% | 21.19% | 1.4 | 0 | 0.080245 | 14.39% | 21.93% | 34.39% | 28.58% | 1.1 | 0 | 0.064992 | 11.65% | 33.4% | 35.45% | 56.18%
| N5 - L2 | 8.237 | 0 | 1.471 | 1.75 | 4.281 | 1.583 | 1.6 | 0.089187 | 0.032979 | 7.981% | 12.43% | 33.45% | 22.33% | 1.4 | 0.087367 | 0.032306 | 9.16% | 17.58% | 37.44% | 30.31% | 1.1 | 0.07076 | 0.026165 | 7.419% | 23.38% | 38.6% | 59.69%
| N5 - L3 | 5.261 | 0 | 2.982 | 0 | 0 | 3.3 | 1.6 | 0 | 0.06875 | 10.99% | 12.99% | 25.78% | 19.96% | 1.4 | 0 | 0.067347 | 11.95% | 18.31% | 28.86% | 26.88% | 1.1 | 0 | 0.054545 | 9.677% | 27.84% | 29.75% | 53.17%
| N5 - L4 | 5.261 | 0 | 0.862 | 1.75 | 4.281 | 0.952 | 1.6 | 0.089187 | 0.019833 | 7.191% | 13.13% | 33.45% | 21.06% | 1.4 | 0.087367 | 0.019429 | 7.816% | 17.58% | 37.44% | 28.55% | 1.1 | 0.07076 | 0.015736 | 6.33% | 23.38% | 38.6% | 56.59%
| N5 - L5 | 2.285 | 0 | 3.591 | 0 | 0 | 3.932 | 1.6 | 0 | 0.081917 | 14.02% | 16.47% | 30.72% | 19.46% | 1.4 | 0 | 0.080245 | 14.39% | 21.93% | 34.39% | 26.29% | 1.1 | 0 | 0.064992 | 11.65% | 33.4% | 35.45% | 52.46%
| N5 - L6 | 2.285 | 0 | 1.471 | 1.75 | 4.281 | 1.583 | 1.6 | 0.089187 | 0.032979 | 8.926% | 13.9% | 33.45% | 20.51% | 1.4 | 0.087367 | 0.032306 | 9.16% | 17.58% | 37.44% | 27.88% | 1.1 | 0.07076 | 0.026165 | 7.419% | 23.38% | 38.6% | 55.74%
| N5 - L7 | 8.097 | 0 | 3.492 | 0.266 | 0.802 | 3.814 | 1.6 | 0.016708 | 0.079458 | 12.26% | 14.33% | 29.8% | 21.53% | 1.4 | 0.016367 | 0.077837 | 14.03% | 21.3% | 33.36% | 29.09% | 1.1 | 0.013256 | 0.063041 | 11.36% | 32.45% | 34.39% | 57.24%
| N5 - L8 | 8.097 | 0 | 1.408 | 2.136 | 5.643 | 1.509 | 1.6 | 0.11756 | 0.031437 | 8.954% | 16.14% | 44.09% | 23.16% | 1.4 | 0.11516 | 0.030796 | 10.25% | 22.68% | 49.36% | 31.62% | 1.1 | 0.093273 | 0.024942 | 8.302% | 29.8% | 50.88% | 62.39%
| N5 - L9 | 5.261 | 0 | 2.912 | 0.057 | 1.155 | 3.212 | 1.6 | 0.024062 | 0.066917 | 10.74% | 12.66% | 25.09% | 20.53% | 1.4 | 0.023571 | 0.065551 | 11.67% | 17.85% | 28.09% | 27.73% | 1.1 | 0.019091 | 0.053091 | 9.452% | 27.16% | 28.96% | 54.92%
| N5 - L10 | 5.261 | 0 | 0.828 | 1.927 | 5.996 | 0.907 | 1.6 | 0.12492 | 0.018896 | 7.731% | 17.46% | 46.84% | 22.14% | 1.4 | 0.12237 | 0.01851 | 8.404% | 23.1% | 52.44% | 30.23% | 1.1 | 0.099107 | 0.014992 | 6.806% | 29.6% | 54.06% | 60.06%
| N5 - L11 | 2.424 | 0 | 3.492 | 0.267 | 0.802 | 3.814 | 1.6 | 0.016708 | 0.079458 | 13.64% | 15.95% | 29.8% | 19.85% | 1.4 | 0.016367 | 0.077837 | 14.03% | 21.3% | 33.36% | 26.87% | 1.1 | 0.013256 | 0.063041 | 11.36% | 32.45% | 34.39% | 53.63%
| N5 - L12 | 2.424 | 0 | 1.408 | 2.136 | 5.643 | 1.509 | 1.6 | 0.11756 | 0.031437 | 9.961% | 17.96% | 44.09% | 21.36% | 1.4 | 0.11516 | 0.030796 | 10.25% | 22.68% | 49.36% | 29.2% | 1.1 | 0.093273 | 0.024942 | 8.302% | 29.8% | 50.88% | 58.45%
| N5 - L13 | 7.958 | 0 | 3.404 | 0.533 | 1.605 | 3.71 | 1.6 | 0.033437 | 0.077292 | 12.09% | 13.99% | 28.98% | 21.89% | 1.4 | 0.032755 | 0.075714 | 13.81% | 20.74% | 32.45% | 29.65% | 1.1 | 0.026529 | 0.061322 | 11.18% | 31.61% | 33.45% | 58.4%
| N5 - L14 | 7.958 | 0 | 1.345 | 2.523 | 7.016 | 1.435 | 1.6 | 0.14617 | 0.029896 | 10.03% | 19.9% | 54.81% | 24.08% | 1.4 | 0.14318 | 0.029286 | 11.46% | 27.81% | 61.36% | 33.07% | 1.1 | 0.11597 | 0.023719 | 9.278% | 36.25% | 63.25% | 65.4%
| N5 - L15 | 5.261 | 0 | 2.852 | 0.114 | 2.31 | 3.138 | 1.6 | 0.048125 | 0.065375 | 10.52% | 12.38% | 24.52% | 21.14% | 1.4 | 0.047143 | 0.064041 | 11.44% | 17.46% | 27.45% | 28.67% | 1.1 | 0.038182 | 0.051868 | 9.262% | 26.57% | 28.29% | 56.83%
| N5 - L16 | 5.26 | 0 | 0.793 | 2.104 | 7.721 | 0.863 | 1.6 | 0.16085 | 0.017979 | 8.288% | 21.82% | 60.32% | 23.36% | 1.4 | 0.15757 | 0.017612 | 9.009% | 28.64% | 67.53% | 32.15% | 1.1 | 0.12762 | 0.014264 | 7.297% | 35.85% | 69.61% | 64.03%
| N5 - L17 | 2.564 | 0 | 3.404 | 0.533 | 1.605 | 3.71 | 1.6 | 0.033437 | 0.077292 | 13.38% | 15.48% | 28.98% | 20.27% | 1.4 | 0.032755 | 0.075714 | 13.81% | 20.74% | 32.45% | 27.49% | 1.1 | 0.026529 | 0.061322 | 11.18% | 31.61% | 33.45% | 54.88%
| N5 - L18 | 2.564 | 0 | 1.345 | 2.523 | 7.016 | 1.435 | 1.6 | 0.14617 | 0.029896 | 11.1% | 22.02% | 54.81% | 22.3% | 1.4 | 0.14318 | 0.029286 | 11.46% | 27.81% | 61.36% | 30.67% | 1.1 | 0.11597 | 0.023719 | 9.278% | 36.25% | 63.25% | 61.46%
| N5 - L19 | 7.958 | 0 | 3.404 | 0 | 0 | 3.71 | 1.6 | 0 | 0.077292 | 11.94% | 13.99% | 28.98% | 20.97% | 1.4 | 0 | 0.075714 | 13.64% | 20.74% | 32.45% | 28.26% | 1.1 | 0 | 0.061322 | 11.05% | 31.61% | 33.45% | 55.58%
| N5 - L20 | 7.958 | 0 | 1.345 | 1.99 | 5.411 | 1.435 | 1.6 | 0.11273 | 0.029896 | 8.427% | 15.42% | 42.27% | 22.91% | 1.4 | 0.11043 | 0.029286 | 9.624% | 21.58% | 47.33% | 31.23% | 1.1 | 0.089438 | 0.023719 | 7.794% | 28.22% | 48.78% | 61.63%
| N5 - L21 | 5.261 | 0 | 2.852 | 0 | 0 | 3.138 | 1.6 | 0 | 0.065375 | 10.51% | 12.38% | 24.52% | 19.87% | 1.4 | 0 | 0.064041 | 11.43% | 17.46% | 27.45% | 26.74% | 1.1 | 0 | 0.051868 | 9.255% | 26.57% | 28.29% | 52.89%
| N5 - L22 | 5.261 | 0 | 0.793 | 1.99 | 5.411 | 0.863 | 1.6 | 0.11273 | 0.017979 | 7.896% | 16.2% | 42.27% | 21.73% | 1.4 | 0.11043 | 0.017612 | 8.583% | 21.58% | 47.33% | 29.58% | 1.1 | 0.089438 | 0.014264 | 6.952% | 28.22% | 48.78% | 58.72%
| N5 - L23 | 2.564 | 0 | 3.404 | 0 | 0 | 3.71 | 1.6 | 0 | 0.077292 | 13.22% | 15.48% | 28.98% | 19.42% | 1.4 | 0 | 0.075714 | 13.64% | 20.74% | 32.45% | 26.21% | 1.1 | 0 | 0.061322 | 11.05% | 31.61% | 33.45% | 52.24%
| N5 - L24 | 2.564 | 0 | 1.345 | 1.99 | 5.411 | 1.435 | 1.6 | 0.11273 | 0.029896 | 9.326% | 17.07% | 42.27% | 21.21% | 1.4 | 0.11043 | 0.029286 | 9.624% | 21.58% | 47.33% | 28.96% | 1.1 | 0.089438 | 0.023719 | 7.794% | 28.22% | 48.78% | 57.92%
| N5 - L25 | 6.438 | 0 | 2.73 | 0 | 0 | 2.909 | 1.6 | 0 | 0.060604 | 9.846% | 11.38% | 22.73% | 20.07% | 1.4 | 0 | 0.059367 | 10.94% | 16.44% | 25.44% | 26.98% | 1.1 | 0 | 0.048083 | 8.859% | 25.15% | 26.23% | 53.2%
| N5 - L26 | 6.437 | 0 | 0.129 | 2.287 | 6.387 | 0 | 1.6 | 0.13306 | 0 | 8.261% | 18.6% | 49.9% | 22.25% | 1.4 | 0.13035 | 0 | 9.178% | 25.29% | 55.86% | 30.34% | 1.1 | 0.10557 | 0 | 7.433% | 32.94% | 57.58% | 60.08%
| N5 - L27 | 5.261 | 0 | 3.474 | 0.262 | 1.212 | 3.824 | 1.6 | 0.02525 | 0.079667 | 12.84% | 15.09% | 29.87% | 20.92% | 1.4 | 0.024735 | 0.078041 | 13.96% | 21.28% | 33.45% | 28.34% | 1.1 | 0.020033 | 0.063207 | 11.31% | 32.37% | 34.48% | 56.16%
| N5 - L28 | 5.261 | 0 | 1.354 | 1.727 | 6.623 | 1.476 | 1.6 | 0.13798 | 0.03075 | 8.089% | 18.58% | 51.74% | 22.93% | 1.4 | 0.13516 | 0.030122 | 8.793% | 24.34% | 57.93% | 31.46% | 1.1 | 0.10947 | 0.024397 | 7.121% | 30.28% | 59.71% | 62.58%
| N5 - L29 | 8.649 | 0 | 3.771 | 0 | 0 | 4.128 | 1.6 | 0 | 0.086 | 13.07% | 15.35% | 32.25% | 21.43% | 1.4 | 0 | 0.084245 | 15.11% | 23.03% | 36.1% | 28.92% | 1.1 | 0 | 0.068231 | 12.24% | 35.07% | 37.22% | 56.81%
| N5 - L30 | 8.649 | 0 | 1.544 | 1.837 | 4.495 | 1.662 | 1.6 | 0.093646 | 0.034625 | 8.317% | 12.96% | 35.12% | 22.64% | 1.4 | 0.091735 | 0.033918 | 9.615% | 18.46% | 39.31% | 30.77% | 1.1 | 0.074298 | 0.027471 | 7.787% | 24.55% | 40.53% | 60.56%
| N5 - L31 | 5.524 | 0 | 3.131 | 0 | 0 | 3.465 | 1.6 | 0 | 0.072187 | 11.48% | 13.58% | 27.07% | 20.13% | 1.4 | 0 | 0.070714 | 12.55% | 19.23% | 30.31% | 27.12% | 1.1 | 0 | 0.057273 | 10.16% | 29.23% | 31.24% | 53.63%
| N5 - L32 | 5.524 | 0 | 0.905 | 1.837 | 4.495 | 0.999 | 1.6 | 0.093646 | 0.020812 | 7.512% | 13.72% | 35.12% | 21.3% | 1.4 | 0.091735 | 0.020388 | 8.205% | 18.46% | 39.31% | 28.9% | 1.1 | 0.074298 | 0.016512 | 6.645% | 24.55% | 40.53% | 57.27%
| N5 - L33 | 2.399 | 0 | 3.771 | 0 | 0 | 4.128 | 1.6 | 0 | 0.086 | 14.69% | 17.25% | 32.25% | 19.61% | 1.4 | 0 | 0.084245 | 15.11% | 23.03% | 36.1% | 26.51% | 1.1 | 0 | 0.068231 | 12.24% | 35.07% | 37.22% | 52.88%
| N5 - L34 | 2.399 | 0 | 1.544 | 1.837 | 4.495 | 1.662 | 1.6 | 0.093646 | 0.034625 | 9.348% | 14.57% | 35.12% | 20.72% | 1.4 | 0.091735 | 0.033918 | 9.615% | 18.46% | 39.31% | 28.2% | 1.1 | 0.074298 | 0.027471 | 7.787% | 24.55% | 40.53% | 56.37%
| N5 - L35 | 8.502 | 0 | 3.667 | 0.28 | 0.843 | 4.005 | 1.6 | 0.017562 | 0.083437 | 12.78% | 14.94% | 31.29% | 21.79% | 1.4 | 0.017204 | 0.081735 | 14.74% | 22.37% | 35.03% | 29.47% | 1.1 | 0.013934 | 0.066198 | 11.93% | 34.08% | 36.11% | 57.95%
| N5 - L36 | 8.502 | 0 | 1.478 | 2.243 | 5.925 | 1.585 | 1.6 | 0.12344 | 0.033021 | 9.334% | 16.83% | 46.29% | 23.54% | 1.4 | 0.12092 | 0.032347 | 10.76% | 23.81% | 51.82% | 32.18% | 1.1 | 0.097934 | 0.026198 | 8.717% | 31.29% | 53.42% | 63.47%
| N5 - L37 | 5.524 | 0 | 3.057 | 0.06 | 1.213 | 3.373 | 1.6 | 0.025271 | 0.070271 | 11.22% | 13.23% | 26.35% | 20.73% | 1.4 | 0.024755 | 0.068837 | 12.25% | 18.75% | 29.5% | 28.03% | 1.1 | 0.02005 | 0.055752 | 9.922% | 28.51% | 30.41% | 55.49%
| N5 - L38 | 5.524 | 0 | 0.869 | 2.023 | 6.296 | 0.953 | 1.6 | 0.13117 | 0.019854 | 8.076% | 18.25% | 49.19% | 22.46% | 1.4 | 0.12849 | 0.019449 | 8.822% | 24.25% | 55.07% | 30.71% | 1.1 | 0.10407 | 0.015752 | 7.145% | 31.08% | 56.76% | 61%
| N5 - L39 | 2.545 | 0 | 3.667 | 0.28 | 0.843 | 4.005 | 1.6 | 0.017562 | 0.083437 | 14.28% | 16.71% | 31.29% | 20.02% | 1.4 | 0.017204 | 0.081735 | 14.74% | 22.37% | 35.03% | 27.12% | 1.1 | 0.013934 | 0.066198 | 11.93% | 34.08% | 36.11% | 54.12%
| N5 - L40 | 2.545 | 0 | 1.478 | 2.243 | 5.925 | 1.585 | 1.6 | 0.12344 | 0.033021 | 10.43% | 18.81% | 46.29% | 21.63% | 1.4 | 0.12092 | 0.032347 | 10.76% | 23.81% | 51.82% | 29.61% | 1.1 | 0.097934 | 0.026198 | 8.717% | 31.29% | 53.42% | 59.28%
| N5 - L41 | 8.356 | 0 | 3.574 | 0.56 | 1.685 | 3.895 | 1.6 | 0.035104 | 0.081146 | 12.6% | 14.58% | 30.43% | 22.17% | 1.4 | 0.034388 | 0.07949 | 14.49% | 21.78% | 34.07% | 30.07% | 1.1 | 0.027851 | 0.06438 | 11.74% | 33.19% | 35.12% | 59.18%
| N5 - L42 | 8.355 | 0 | 1.412 | 2.649 | 7.367 | 1.507 | 1.6 | 0.15348 | 0.031396 | 10.46% | 20.75% | 57.55% | 24.54% | 1.4 | 0.15035 | 0.030755 | 12.03% | 29.2% | 64.43% | 33.76% | 1.1 | 0.12177 | 0.024909 | 9.741% | 38.06% | 66.42% | 66.73%
| N5 - L43 | 5.524 | 0 | 2.994 | 0.12 | 2.425 | 3.294 | 1.6 | 0.050521 | 0.068625 | 10.99% | 12.94% | 25.73% | 21.38% | 1.4 | 0.04949 | 0.067224 | 12.01% | 18.33% | 28.81% | 29.02% | 1.1 | 0.040083 | 0.054446 | 9.724% | 27.89% | 29.7% | 57.51%
| N5 - L44 | 5.523 | 0 | 0.833 | 2.209 | 8.107 | 0.906 | 1.6 | 0.1689 | 0.018875 | 8.66% | 22.8% | 63.34% | 23.78% | 1.4 | 0.16545 | 0.01849 | 9.459% | 30.08% | 70.91% | 32.79% | 1.1 | 0.134 | 0.014975 | 7.661% | 37.64% | 73.09% | 65.3%
| N5 - L45 | 2.692 | 0 | 3.574 | 0.56 | 1.685 | 3.895 | 1.6 | 0.035104 | 0.081146 | 14.01% | 16.21% | 30.43% | 20.46% | 1.4 | 0.034388 | 0.07949 | 14.49% | 21.78% | 34.07% | 27.78% | 1.1 | 0.027851 | 0.06438 | 11.74% | 33.19% | 35.12% | 55.45%
| N5 - L46 | 2.692 | 0 | 1.413 | 2.649 | 7.366 | 1.507 | 1.6 | 0.15346 | 0.031396 | 11.63% | 23.06% | 57.55% | 22.64% | 1.4 | 0.15033 | 0.030755 | 12.03% | 29.2% | 64.43% | 31.19% | 1.1 | 0.12175 | 0.024909 | 9.743% | 38.06% | 66.41% | 62.53%
| N5 - L47 | 8.356 | 0 | 3.574 | 0 | 0 | 3.895 | 1.6 | 0 | 0.081146 | 12.45% | 14.58% | 30.43% | 21.2% | 1.4 | 0 | 0.07949 | 14.32% | 21.78% | 34.07% | 28.59% | 1.1 | 0 | 0.06438 | 11.6% | 33.19% | 35.12% | 56.18%
| N5 - L48 | 8.355 | 0 | 1.412 | 2.089 | 5.681 | 1.507 | 1.6 | 0.11835 | 0.031396 | 8.784% | 16.08% | 44.38% | 23.27% | 1.4 | 0.11594 | 0.030755 | 10.1% | 22.65% | 49.69% | 31.77% | 1.1 | 0.093901 | 0.024909 | 8.182% | 29.63% | 51.22% | 62.65%
| N5 - L49 | 5.524 | 0 | 2.994 | 0 | 0 | 3.294 | 1.6 | 0 | 0.068625 | 10.98% | 12.94% | 25.73% | 20.03% | 1.4 | 0 | 0.067224 | 12% | 18.33% | 28.81% | 26.97% | 1.1 | 0 | 0.054446 | 9.716% | 27.89% | 29.7% | 53.32%
| N5 - L50 | 5.524 | 0 | 0.833 | 2.089 | 5.681 | 0.906 | 1.6 | 0.11835 | 0.018875 | 8.249% | 16.93% | 44.38% | 22.01% | 1.4 | 0.11594 | 0.01849 | 9.011% | 22.65% | 49.69% | 30.01% | 1.1 | 0.093901 | 0.014975 | 7.298% | 29.63% | 51.22% | 59.56%
| N5 - L51 | 2.692 | 0 | 3.574 | 0 | 0 | 3.895 | 1.6 | 0 | 0.081146 | 13.84% | 16.21% | 30.43% | 19.56% | 1.4 | 0 | 0.07949 | 14.32% | 21.78% | 34.07% | 26.42% | 1.1 | 0 | 0.06438 | 11.6% | 33.19% | 35.12% | 52.65%
| N5 - L52 | 2.692 | 0 | 1.413 | 2.089 | 5.681 | 1.507 | 1.6 | 0.11835 | 0.031396 | 9.768% | 17.87% | 44.38% | 21.47% | 1.4 | 0.11594 | 0.030755 | 10.1% | 22.65% | 49.69% | 29.35% | 1.1 | 0.093901 | 0.024909 | 8.184% | 29.63% | 51.22% | 58.71%
| N5 - L53 | 9.013 | 0 | 3.823 | 0 | 0 | 4.072 | 1.6 | 0 | 0.084833 | 13.16% | 15.21% | 31.81% | 21.5% | 1.4 | 0 | 0.083102 | 15.32% | 23.02% | 35.62% | 29.01% | 1.1 | 0 | 0.067306 | 12.41% | 35.22% | 36.71% | 56.93%
| N5 - L54 | 9.012 | 0 | 0.18 | 3.202 | 8.942 | 0 | 1.6 | 0.18629 | 0 | 11.04% | 24.87% | 69.86% | 25.06% | 1.4 | 0.18249 | 0 | 12.85% | 35.41% | 78.21% | 34.58% | 1.1 | 0.1478 | 0 | 10.41% | 46.12% | 80.62% | 68.33%
| N5 - L55 | 6.313 | 0 | 4.169 | 0.315 | 1.454 | 4.589 | 1.6 | 0.030292 | 0.095604 | 15.11% | 17.76% | 35.85% | 21.86% | 1.4 | 0.029673 | 0.093653 | 16.75% | 25.53% | 40.14% | 29.71% | 1.1 | 0.024033 | 0.075851 | 13.57% | 38.85% | 41.37% | 58.8%
| N5 - L56 | 6.313 | 0 | 1.625 | 2.073 | 7.947 | 1.771 | 1.6 | 0.16556 | 0.036896 | 9.521% | 21.87% | 62.09% | 24.48% | 1.4 | 0.16218 | 0.036143 | 10.55% | 29.21% | 69.51% | 33.83% | 1.1 | 0.13136 | 0.029273 | 8.548% | 36.34% | 71.65% | 67.27%
| N6 - L1 | 5.821 | 0 | 2.538 | 0 | 0 | 3.028 | 1.6 | 0 | 0.063083 | 9.258% | 11.45% | 23.66% | 19.97% | 1.4 | 0 | 0.061796 | 10.17% | 16.23% | 26.48% | 26.85% | 1.1 | 0 | 0.05005 | 8.236% | 24.35% | 27.3% | 53.03%
| N6 - L2 | 3.612 | 0 | 0.801 | 1.468 | 3.701 | 1.044 | 1.6 | 0.077104 | 0.02175 | 6.361% | 11.63% | 28.91% | 20.27% | 1.4 | 0.075531 | 0.021306 | 6.7% | 15.07% | 32.37% | 27.43% | 1.1 | 0.061174 | 0.017256 | 5.427% | 19.95% | 33.37% | 54.58%
| N6 - L3 | 7.333 | 0 | 2.725 | 0 | 0 | 3.164 | 1.6 | 0 | 0.065917 | 9.669% | 11.76% | 24.72% | 20.47% | 1.4 | 0 | 0.064571 | 10.92% | 17.17% | 27.67% | 27.53% | 1.1 | 0 | 0.052298 | 8.843% | 25.89% | 28.53% | 54.19%
| N6 - L4 | 5.123 | 0 | 0.988 | 1.468 | 3.701 | 1.18 | 1.6 | 0.077104 | 0.024583 | 6.54% | 11.3% | 28.91% | 20.79% | 1.4 | 0.075531 | 0.024082 | 7.09% | 15.07% | 32.37% | 28.14% | 1.1 | 0.061174 | 0.019504 | 5.742% | 19.95% | 33.37% | 55.79%
| N6 - L5 | 8.797 | 0 | 2.304 | 0 | 0 | 2.786 | 1.6 | 0 | 0.058042 | 7.964% | 9.935% | 21.77% | 20.67% | 1.4 | 0 | 0.056857 | 9.231% | 14.84% | 24.37% | 27.75% | 1.1 | 0 | 0.04605 | 7.477% | 22.22% | 25.12% | 54.4%
| N6 - L6 | 6.588 | 0 | 0.567 | 1.468 | 3.701 | 0.802 | 1.6 | 0.077104 | 0.016708 | 5.66% | 11% | 28.91% | 21.01% | 1.4 | 0.075531 | 0.016367 | 6.305% | 15.07% | 32.37% | 28.4% | 1.1 | 0.061174 | 0.013256 | 5.107% | 19.95% | 33.37% | 56.07%
| N6 - L7 | 5.747 | 0 | 2.472 | 0.133 | 0.395 | 2.942 | 1.6 | 0.0082292 | 0.061292 | 9.043% | 11.15% | 22.98% | 20.1% | 1.4 | 0.0080612 | 0.060041 | 9.919% | 15.78% | 25.73% | 27.06% | 1.1 | 0.0065289 | 0.048628 | 8.033% | 23.7% | 26.52% | 53.47%
| N6 - L8 | 3.592 | 0 | 0.762 | 1.456 | 3.865 | 0.993 | 1.6 | 0.080521 | 0.020687 | 6.254% | 12.01% | 30.2% | 20.33% | 1.4 | 0.078878 | 0.020265 | 6.584% | 15.51% | 33.8% | 27.53% | 1.1 | 0.063884 | 0.016413 | 5.333% | 20.37% | 34.85% | 54.79%
| N6 - L9 | 7.187 | 0 | 2.65 | 0.267 | 0.803 | 3.072 | 1.6 | 0.016729 | 0.064 | 9.475% | 11.46% | 24% | 20.81% | 1.4 | 0.016388 | 0.062694 | 10.67% | 16.68% | 26.87% | 28.06% | 1.1 | 0.013273 | 0.050777 | 8.643% | 25.16% | 27.7% | 55.27%
| N6 - L10 | 5.033 | 0 | 0.941 | 1.855 | 5.063 | 1.123 | 1.6 | 0.10548 | 0.023396 | 7.7% | 15.21% | 39.55% | 21.58% | 1.4 | 0.10333 | 0.022918 | 8.334% | 20.17% | 44.28% | 29.37% | 1.1 | 0.083686 | 0.018562 | 6.75% | 26.37% | 45.65% | 58.31%
| N6 - L11 | 8.583 | 0 | 2.249 | 0.456 | 2.353 | 2.711 | 1.6 | 0.049021 | 0.056479 | 7.962% | 9.715% | 21.18% | 21.9% | 1.4 | 0.04802 | 0.055327 | 9.194% | 14.46% | 23.71% | 29.63% | 1.1 | 0.038893 | 0.04481 | 7.447% | 21.66% | 24.44% | 58.26%
| N6 - L12 | 6.429 | 0 | 0.539 | 2.045 | 6.614 | 0.762 | 1.6 | 0.13779 | 0.015875 | 7.628% | 18.71% | 51.67% | 22.86% | 1.4 | 0.13498 | 0.015551 | 8.474% | 25.24% | 57.85% | 31.28% | 1.1 | 0.10932 | 0.012595 | 6.863% | 32.17% | 59.63% | 62%
| N6 - L13 | 5.677 | 0 | 2.415 | 0.265 | 0.791 | 2.868 | 1.6 | 0.016479 | 0.05975 | 8.886% | 10.9% | 22.41% | 20.25% | 1.4 | 0.016143 | 0.058531 | 9.734% | 15.4% | 25.08% | 27.29% | 1.1 | 0.013074 | 0.047405 | 7.884% | 23.13% | 25.86% | 53.95%
| N6 - L14 | 3.573 | 0 | 0.723 | 1.443 | 4.04 | 0.941 | 1.6 | 0.084167 | 0.019604 | 6.144% | 12.42% | 31.56% | 20.4% | 1.4 | 0.082449 | 0.019204 | 6.467% | 15.99% | 35.34% | 27.64% | 1.1 | 0.066777 | 0.015554 | 5.238% | 20.81% | 36.42% | 55.02%
| N6 - L15 | 7.046 | 0 | 2.585 | 0.533 | 1.605 | 2.992 | 1.6 | 0.033437 | 0.062333 | 9.414% | 11.2% | 23.37% | 21.18% | 1.4 | 0.032755 | 0.061061 | 10.58% | 16.26% | 26.17% | 28.61% | 1.1 | 0.026529 | 0.049455 | 8.565% | 24.53% | 26.98% | 56.43%
| N6 - L16 | 4.943 | 0 | 0.893 | 2.241 | 6.436 | 1.065 | 1.6 | 0.13408 | 0.022187 | 8.946% | 19.16% | 50.28% | 22.44% | 1.4 | 0.13135 | 0.021735 | 9.666% | 25.3% | 56.29% | 30.72% | 1.1 | 0.10638 | 0.017603 | 7.828% | 32.81% | 58.03% | 61.12%
| N6 - L17 | 8.373 | 0 | 2.203 | 0.912 | 4.706 | 2.649 | 1.6 | 0.098042 | 0.055187 | 8.304% | 11.95% | 36.77% | 23.33% | 1.4 | 0.096041 | 0.054061 | 9.553% | 16.38% | 41.16% | 31.84% | 1.1 | 0.077785 | 0.043785 | 7.737% | 21.2% | 42.43% | 62.78%
| N6 - L18 | 6.27 | 0 | 0.511 | 2.621 | 9.537 | 0.722 | 1.6 | 0.19869 | 0.015042 | 9.66% | 26.49% | 74.51% | 25.1% | 1.4 | 0.19463 | 0.014735 | 10.7% | 35.45% | 83.41% | 34.85% | 1.1 | 0.15764 | 0.011934 | 8.666% | 44.41% | 85.98% | 69.43%
| N6 - L19 | 5.677 | 0 | 2.415 | 0 | 0 | 2.868 | 1.6 | 0 | 0.05975 | 8.833% | 10.9% | 22.41% | 19.83% | 1.4 | 0 | 0.058531 | 9.676% | 15.4% | 25.08% | 26.66% | 1.1 | 0 | 0.047405 | 7.837% | 23.13% | 25.86% | 52.67%
| N6 - L20 | 3.573 | 0 | 0.723 | 1.708 | 4.831 | 0.941 | 1.6 | 0.10065 | 0.019604 | 7.061% | 14.81% | 37.74% | 20.88% | 1.4 | 0.098592 | 0.019204 | 7.431% | 19.06% | 42.25% | 28.38% | 1.1 | 0.079851 | 0.015554 | 6.019% | 24.78% | 43.56% | 56.54%
| N6 - L21 | 7.046 | 0 | 2.585 | 0 | 0 | 2.992 | 1.6 | 0 | 0.062333 | 9.22% | 11.2% | 23.37% | 20.29% | 1.4 | 0 | 0.061061 | 10.36% | 16.26% | 26.17% | 27.28% | 1.1 | 0 | 0.049455 | 8.389% | 24.53% | 26.98% | 53.71%
| N6 - L22 | 4.943 | 0 | 0.893 | 1.708 | 4.831 | 1.065 | 1.6 | 0.10065 | 0.022187 | 7.147% | 14.43% | 37.74% | 21.37% | 1.4 | 0.098592 | 0.021735 | 7.722% | 19.06% | 42.25% | 29.05% | 1.1 | 0.079851 | 0.017603 | 6.254% | 24.78% | 43.56% | 57.67%
| N6 - L23 | 8.373 | 0 | 2.203 | 0 | 0 | 2.649 | 1.6 | 0 | 0.055187 | 7.672% | 9.537% | 20.7% | 20.47% | 1.4 | 0 | 0.054061 | 8.827% | 14.15% | 23.17% | 27.47% | 1.1 | 0 | 0.043785 | 7.149% | 21.2% | 23.88% | 53.9%
| N6 - L24 | 6.27 | 0 | 0.511 | 1.708 | 4.831 | 0.722 | 1.6 | 0.10065 | 0.015042 | 6.45% | 14.08% | 37.74% | 21.58% | 1.4 | 0.098592 | 0.014735 | 7.143% | 19.06% | 42.25% | 29.29% | 1.1 | 0.079851 | 0.011934 | 5.785% | 24.78% | 43.56% | 57.94%
| N6 - L25 | 6.858 | 0 | 2.073 | 0 | 0 | 2.383 | 1.6 | 0 | 0.049646 | 7.419% | 8.973% | 18.62% | 19.9% | 1.4 | 0 | 0.048633 | 8.306% | 12.99% | 20.84% | 26.69% | 1.1 | 0 | 0.039388 | 6.727% | 19.62% | 21.48% | 52.54%
| N6 - L26 | 3.994 | 0 | 0.033 | 1.968 | 5.722 | 0.054 | 1.6 | 0.11921 | 0.001125 | 7.432% | 17.3% | 44.7% | 21.08% | 1.4 | 0.11678 | 0.001102 | 7.886% | 22.42% | 50.05% | 28.68% | 1.1 | 0.094579 | 0.00089256 | 6.387% | 29.02% | 51.59% | 57.1%
| N6 - L27 | 7.46 | 0 | 2.584 | 0.131 | 0.894 | 3.073 | 1.6 | 0.018625 | 0.064021 | 9.159% | 11.29% | 24.01% | 20.94% | 1.4 | 0.018245 | 0.062714 | 10.37% | 16.49% | 26.88% | 28.24% | 1.1 | 0.014777 | 0.050793 | 8.396% | 24.77% | 27.71% | 55.6%
| N6 - L28 | 5.251 | 0 | 0.847 | 1.84 | 5.725 | 1.089 | 1.6 | 0.11927 | 0.022687 | 7.468% | 16.68% | 44.73% | 22.06% | 1.4 | 0.11684 | 0.022224 | 8.116% | 22.06% | 50.07% | 30.11% | 1.1 | 0.094628 | 0.018 | 6.573% | 28.26% | 51.62% | 59.8%
| N6 - L29 | 6.112 | 0 | 2.665 | 0 | 0 | 3.179 | 1.6 | 0 | 0.066229 | 9.669% | 11.96% | 24.84% | 20.13% | 1.4 | 0 | 0.064878 | 10.68% | 17.04% | 27.8% | 27.09% | 1.1 | 0 | 0.052545 | 8.648% | 25.57% | 28.66% | 53.48%
| N6 - L30 | 3.792 | 0 | 0.841 | 1.542 | 3.886 | 1.096 | 1.6 | 0.080958 | 0.022833 | 6.658% | 12.17% | 30.36% | 20.46% | 1.4 | 0.079306 | 0.022367 | 7.038% | 15.83% | 33.99% | 27.72% | 1.1 | 0.064231 | 0.018116 | 5.7% | 20.95% | 35.04% | 55.13%
| N6 - L31 | 7.699 | 0 | 2.861 | 0 | 0 | 3.322 | 1.6 | 0 | 0.069208 | 10.08% | 12.27% | 25.95% | 20.67% | 1.4 | 0 | 0.067796 | 11.46% | 18.03% | 29.06% | 27.81% | 1.1 | 0 | 0.054909 | 9.284% | 27.18% | 29.95% | 54.7%
| N6 - L32 | 5.379 | 0 | 1.038 | 1.542 | 3.886 | 1.239 | 1.6 | 0.080958 | 0.025812 | 6.837% | 11.81% | 30.36% | 21.01% | 1.4 | 0.079306 | 0.025286 | 7.448% | 15.83% | 33.99% | 28.47% | 1.1 | 0.064231 | 0.020479 | 6.032% | 20.95% | 35.04% | 56.41%
| N6 - L33 | 9.237 | 0 | 2.419 | 0 | 0 | 2.925 | 1.6 | 0 | 0.060937 | 8.297% | 10.35% | 22.85% | 20.87% | 1.4 | 0 | 0.059694 | 9.692% | 15.58% | 25.58% | 28.03% | 1.1 | 0 | 0.048347 | 7.85% | 23.33% | 26.37% | 54.92%
| N6 - L34 | 6.917 | 0 | 0.595 | 1.542 | 3.886 | 0.842 | 1.6 | 0.080958 | 0.017542 | 5.909% | 11.48% | 30.36% | 21.24% | 1.4 | 0.079306 | 0.017184 | 6.622% | 15.83% | 33.99% | 28.73% | 1.1 | 0.064231 | 0.013917 | 5.364% | 20.95% | 35.04% | 56.7%
| N6 - L35 | 6.034 | 0 | 2.595 | 0.139 | 0.415 | 3.089 | 1.6 | 0.0086458 | 0.064354 | 9.442% | 11.65% | 24.13% | 20.28% | 1.4 | 0.0084694 | 0.063041 | 10.41% | 16.57% | 27.02% | 27.31% | 1.1 | 0.0068595 | 0.051058 | 8.433% | 24.88% | 27.85% | 53.94%
| N6 - L36 | 3.772 | 0 | 0.8 | 1.528 | 4.059 | 1.042 | 1.6 | 0.084562 | 0.021708 | 6.541% | 12.57% | 31.71% | 20.52% | 1.4 | 0.082837 | 0.021265 | 6.911% | 16.29% | 35.5% | 27.82% | 1.1 | 0.067091 | 0.017223 | 5.597% | 21.38% | 36.6% | 55.35%
| N6 - L37 | 7.547 | 0 | 2.783 | 0.28 | 0.843 | 3.225 | 1.6 | 0.017562 | 0.067187 | 9.886% | 11.95% | 25.2% | 21.03% | 1.4 | 0.017204 | 0.065816 | 11.21% | 17.52% | 28.21% | 28.37% | 1.1 | 0.013934 | 0.053306 | 9.077% | 26.42% | 29.08% | 55.85%
| N6 - L38 | 5.285 | 0 | 0.988 | 1.948 | 5.317 | 1.179 | 1.6 | 0.11077 | 0.024562 | 8.048% | 15.9% | 41.54% | 21.86% | 1.4 | 0.10851 | 0.024061 | 8.752% | 21.18% | 46.5% | 29.78% | 1.1 | 0.087884 | 0.019488 | 7.088% | 27.69% | 47.94% | 59.12%
| N6 - L39 | 9.012 | 0 | 2.361 | 0.479 | 2.471 | 2.847 | 1.6 | 0.051479 | 0.059312 | 8.296% | 10.12% | 22.24% | 22.19% | 1.4 | 0.050429 | 0.058102 | 9.653% | 15.18% | 24.9% | 30.04% | 1.1 | 0.040843 | 0.047058 | 7.818% | 22.75% | 25.67% | 59.02%
| N6 - L40 | 6.75 | 0 | 0.566 | 2.147 | 6.944 | 0.8 | 1.6 | 0.14467 | 0.016667 | 7.962% | 19.53% | 54.25% | 23.23% | 1.4 | 0.14171 | 0.016327 | 8.896% | 26.5% | 60.73% | 31.83% | 1.1 | 0.11478 | 0.013223 | 7.205% | 33.77% | 62.61% | 63.08%
| N6 - L41 | 5.96 | 0 | 2.536 | 0.279 | 0.83 | 3.011 | 1.6 | 0.017292 | 0.062729 | 9.283% | 11.38% | 23.52% | 20.44% | 1.4 | 0.016939 | 0.061449 | 10.22% | 16.17% | 26.34% | 27.55% | 1.1 | 0.013719 | 0.049769 | 8.279% | 24.29% | 27.15% | 54.45%
| N6 - L42 | 3.752 | 0 | 0.759 | 1.515 | 4.242 | 0.988 | 1.6 | 0.088375 | 0.020583 | 6.428% | 12.99% | 33.14% | 20.6% | 1.4 | 0.086571 | 0.020163 | 6.789% | 16.78% | 37.1% | 27.94% | 1.1 | 0.070116 | 0.016331 | 5.499% | 21.85% | 38.24% | 55.59%
| N6 - L43 | 7.399 | 0 | 2.715 | 0.56 | 1.685 | 3.141 | 1.6 | 0.035104 | 0.065437 | 9.824% | 11.68% | 24.54% | 21.42% | 1.4 | 0.034388 | 0.064102 | 11.11% | 17.07% | 27.47% | 28.96% | 1.1 | 0.027851 | 0.051917 | 8.996% | 25.76% | 28.32% | 57.08%
| N6 - L44 | 5.19 | 0 | 0.937 | 2.353 | 6.758 | 1.118 | 1.6 | 0.14079 | 0.023292 | 9.348% | 20.03% | 52.8% | 22.78% | 1.4 | 0.13792 | 0.022816 | 10.15% | 26.56% | 59.11% | 31.24% | 1.1 | 0.1117 | 0.018479 | 8.219% | 34.45% | 60.93% | 62.14%
| N6 - L45 | 8.792 | 0 | 2.314 | 0.958 | 4.941 | 2.781 | 1.6 | 0.10294 | 0.057937 | 8.658% | 12.46% | 38.6% | 23.71% | 1.4 | 0.10084 | 0.056755 | 10.03% | 17.2% | 43.22% | 32.41% | 1.1 | 0.081669 | 0.045967 | 8.127% | 22.27% | 44.55% | 63.87%
| N6 - L46 | 6.584 | 0 | 0.536 | 2.752 | 10.013 | 0.758 | 1.6 | 0.2086 | 0.015792 | 10.08% | 27.66% | 78.23% | 25.65% | 1.4 | 0.20435 | 0.015469 | 11.23% | 37.22% | 87.58% | 35.73% | 1.1 | 0.1655 | 0.012529 | 9.098% | 46.63% | 90.27% | 71.18%
| N6 - L47 | 5.96 | 0 | 2.536 | 0 | 0 | 3.011 | 1.6 | 0 | 0.062729 | 9.227% | 11.38% | 23.52% | 19.99% | 1.4 | 0 | 0.061449 | 10.16% | 16.17% | 26.34% | 26.89% | 1.1 | 0 | 0.049769 | 8.23% | 24.29% | 27.15% | 53.09%
| N6 - L48 | 3.752 | 0 | 0.759 | 1.794 | 5.072 | 0.988 | 1.6 | 0.10567 | 0.020583 | 7.39% | 15.5% | 39.62% | 21.11% | 1.4 | 0.10351 | 0.020163 | 7.805% | 20.02% | 44.36% | 28.73% | 1.1 | 0.083835 | 0.016331 | 6.321% | 26.03% | 45.73% | 57.23%
| N6 - L49 | 7.398 | 0 | 2.715 | 0 | 0 | 3.141 | 1.6 | 0 | 0.065437 | 9.622% | 11.68% | 24.54% | 20.48% | 1.4 | 0 | 0.064102 | 10.88% | 17.07% | 27.47% | 27.54% | 1.1 | 0 | 0.051917 | 8.81% | 25.76% | 28.32% | 54.19%
| N6 - L50 | 5.19 | 0 | 0.937 | 1.794 | 5.072 | 1.118 | 1.6 | 0.10567 | 0.023292 | 7.471% | 15.08% | 39.62% | 21.63% | 1.4 | 0.10351 | 0.022816 | 8.109% | 20.02% | 44.36% | 29.44% | 1.1 | 0.083835 | 0.018479 | 6.568% | 26.03% | 45.73% | 58.43%
| N6 - L51 | 8.792 | 0 | 2.314 | 0 | 0 | 2.781 | 1.6 | 0 | 0.057937 | 7.999% | 9.941% | 21.73% | 20.66% | 1.4 | 0 | 0.056755 | 9.272% | 14.85% | 24.32% | 27.74% | 1.1 | 0 | 0.045967 | 7.509% | 22.27% | 25.07% | 54.39%
| N6 - L52 | 6.584 | 0 | 0.536 | 1.794 | 5.072 | 0.758 | 1.6 | 0.10567 | 0.015792 | 6.735% | 14.7% | 39.62% | 21.85% | 1.4 | 0.10351 | 0.015469 | 7.502% | 20.02% | 44.36% | 29.69% | 1.1 | 0.083835 | 0.012529 | 6.076% | 26.03% | 45.73% | 58.71%
| N6 - L53 | 9.601 | 0 | 2.902 | 0 | 0 | 3.336 | 1.6 | 0 | 0.0695 | 9.891% | 11.96% | 26.06% | 21.22% | 1.4 | 0 | 0.068082 | 11.63% | 18.19% | 29.18% | 28.54% | 1.1 | 0 | 0.05514 | 9.417% | 27.47% | 30.08% | 55.89%
| N6 - L54 | 5.592 | 0 | 0.046 | 2.755 | 8.011 | 0.076 | 1.6 | 0.1669 | 0.0015833 | 10.09% | 23.5% | 62.59% | 23.21% | 1.4 | 0.16349 | 0.001551 | 11.04% | 31.39% | 70.07% | 31.91% | 1.1 | 0.13241 | 0.0012562 | 8.942% | 40.63% | 72.23% | 63.47%
| N6 - L55 | 8.952 | 0 | 3.101 | 0.157 | 1.073 | 3.688 | 1.6 | 0.022354 | 0.076833 | 10.7% | 13.2% | 28.81% | 21.86% | 1.4 | 0.021898 | 0.075265 | 12.44% | 19.79% | 32.26% | 29.55% | 1.1 | 0.017736 | 0.060959 | 10.08% | 29.72% | 33.25% | 58.03%
| N6 - L56 | 6.301 | 0 | 1.017 | 2.207 | 6.87 | 1.307 | 1.6 | 0.14312 | 0.027229 | 8.786% | 19.62% | 53.67% | 23.34% | 1.4 | 0.1402 | 0.026673 | 9.736% | 26.46% | 60.09% | 32.04% | 1.1 | 0.11355 | 0.021603 | 7.886% | 33.91% | 61.94% | 63.58%
132kV CT Structure x 2400mm high
132kV CVT Structure x 2400mm high | MAX | 7.83 |  | 3.59 | 2.53 | 7.18 | 14.88 | 1.7 |  | Worst Load Case = | 11.86% | 34.78% | 96.92% | 26.72% | 1.6 |  | Worst Load Case = | 11.01% | 36.07% | 87.19% | 33.65% | 1.3 |  | Worst Load Case = | 8.341% | 40.16% | 81.27% | 64.57%
| 1 | 5.01 | 0 | 1.91 | 1.64 | 4.63 | 10.24 | 1.7 | 0.085444 | 0.18897 | 8.349% | 23.2% | 66.7% | 25.78% | 1.6 | 0.072344 | 0.16 | 7.723% | 23.73% | 60% | 32.71% | 1.3 | 0.054793 | 0.12118 | 5.849% | 25.6% | 55.93% | 63.06%
| 2 | 5.01 | 0 | 3.42 | 0 | 0 | 14.18 | 1.7 | 0 | 0.26168 | 11.34% | 33.28% | 92.36% | 26.05% | 1.6 | 0 | 0.22156 | 10.49% | 34.37% | 83.09% | 32.92% | 1.3 | 0 | 0.16781 | 7.946% | 38.27% | 77.45% | 63.32%
| 3 | 5.6 | 0 | 0.58 | 1.81 | 5.13 | 3.13 | 1.7 | 0.094671 | 0.057762 | 6.241% | 12.77% | 33.41% | 21.93% | 1.6 | 0.080156 | 0.048906 | 5.831% | 13.55% | 30.06% | 28.36% | 1.3 | 0.06071 | 0.037041 | 4.416% | 15.93% | 28.02% | 55.22%
| 4 | 5.6 | 0 | 2.07 | 0 | 0 | 6.55 | 1.7 | 0 | 0.12088 | 6.797% | 15.94% | 42.66% | 21.18% | 1.6 | 0 | 0.10234 | 6.35% | 16.84% | 38.38% | 27.47% | 1.3 | 0 | 0.077515 | 4.809% | 19.46% | 35.78% | 53.6%
| 5 | 5.26 | 0 | 2 | 1.73 | 4.86 | 10.75 | 1.7 | 0.089689 | 0.19839 | 8.733% | 24.24% | 70.02% | 26.38% | 1.6 | 0.075937 | 0.16797 | 8.112% | 24.9% | 62.99% | 33.38% | 1.3 | 0.057515 | 0.12722 | 6.144% | 26.85% | 58.72% | 64.21%
| 6 | 5.26 | 0 | 3.59 | 0 | 0 | 14.88 | 1.7 | 0 | 0.2746 | 11.86% | 34.78% | 96.92% | 26.72% | 1.6 | 0 | 0.2325 | 11.01% | 36.07% | 87.19% | 33.65% | 1.3 | 0 | 0.17609 | 8.341% | 40.16% | 81.27% | 64.57%
| 7 | 7.83 | 0 | 0.81 | 2.53 | 7.18 | 4.38 | 1.7 | 0.1325 | 0.08083 | 8.41% | 17.22% | 46.77% | 24.46% | 1.6 | 0.11219 | 0.068437 | 8.149% | 18.96% | 42.07% | 31.21% | 1.3 | 0.08497 | 0.051834 | 6.172% | 22.28% | 39.22% | 60.11%
| 8 | 7.83 | 0 | 2.9 | 0 | 0 | 9.16 | 1.7 | 0 | 0.16904 | 9.181% | 21.5% | 59.66% | 23.32% | 1.6 | 0 | 0.14312 | 8.896% | 23.55% | 53.67% | 29.89% | 1.3 | 0 | 0.1084 | 6.738% | 27.24% | 50.03% | 57.71%
132V Cable Sealing End
132kV Circuit Breaker

## Graph data (ss) (hidden)
| 0.75m | 1m | 2m
400kV High Level - Post Insulator Structure x 7150mm high | 3.7 | 3.4 | 2.7
400kV CT Structure x 2400mm high | 2.7 | 2.7 | 2.2
400kV 3 Phase Pantograph Disconnector x 2400mm high | 2.7 | 2.5 | 2
400kV Earth Switch Structure x 2900mm high | 2.4 | 2.2 | 1.8
400kV Disconnector with 2 Earth Switch Structure x 2500mm high | 1.8 | 1.8 | 1.4
400kV Low Level - Post Insulator Structure x 2750mm high | 1.7 | 1.6 | 1.4
400kV Surge Arrester Structure x 2400mm high | 2.3 | 2.1 | 1.7
400kV CVT Structure x 2400mm high | 2 | 1.9 | 1.5
132kV Earth Switch Structure x 2600mm high | 1.6 | 1.4 | 1.1
132kV High Level - Surge Arrester Structure x 6000mm high | 1.7 | 1.6 | 1.3
132kV CVT Structure x 2400mm high | 1.7 | 1.6 | 1.3
132kV Low Level - Surge Arrester Structure x 2400mm high | 1.5 | 1.4 | 1.1

## Loading Summary
Name | Loadcase | Vertical Fz (kN) | Beneficial Vertical (kN) | ¦¦ to Span, Fy (kN) | ⊥ to Span, Fx (kN) | Moment about ¦¦, My (kNm) | Moment about ⊥, Mx (kNm)
400kV High Level - Post Insulator Structure x 7150mm high | 1 | 17.37 | 0 | 0 | 13.88 | 137.78 | 0
400kV High Level - Post Insulator Structure x 7150mm high | 2 | 17.37 | 0 | 4.24 | 5.6 | 66.39 | 23.66
400kV Surge Arrester Structure x 2400mm high | 1 | 5.77 | 0 | 3.71 | 2.11 | 7.88 | 27.4
400kV Surge Arrester Structure x 2400mm high | 2 | 5.77 | 0 | 0.63 | 0 | 0 | 33.98
400kV Earth Switch Structure x 2900mm high | N4 - L1 | 3.937 | 0 | 1.26 | 0 | 0 | 5.292
400kV Earth Switch Structure x 2900mm high | N4 - L2 | 7.519 | 0 | 1.626 | 2.801 | 9.919 | 0.034
400kV Disconnector with 2 Earth Switch Structure x 2500mm high | N7 - L1 | 9.164 | 0 | 0.69 | 0.392 | 0.269 | 8.97
400kV Disconnector with 2 Earth Switch Structure x 2500mm high | N7 - L2 | 10.49 | 0 | 3.257 | 3.368 | 9.029 | 0.961
400kV CT Structure x 2400mm high | 1 | 33.38 | 0 | 0 | 10.39 | 68.08 | 0
400kV CT Structure x 2400mm high | 2 | 33.38 | 0 | 4.41 | 4.65 | 36.8 | 20.7
132kV High Level - Surge Arrester Structure x 6000mm high | 1 | 2.62 | 0 | 1.67 | 1.66 | 4.89 | 10.21
132kV High Level - Surge Arrester Structure x 6000mm high | 2 | 2.62 | 0 | 3.1 | 0 | 0 | 13.7
132kV Earth Switch Structure x 2600mm high | N4 - L1 | 2.325 | 0 | 2.255 | 0 | 0 | 2.74
132kV Earth Switch Structure x 2600mm high | N4 - L2 | 0.115 | 0 | 0.518 | 1.474 | 3.717 | 0.756
132kV CVT Structure x 2400mm high | 1 | 5.01 | 0 | 1.91 | 1.64 | 4.63 | 10.24
132kV CVT Structure x 2400mm high | 2 | 5.01 | 0 | 3.42 | 0 | 0 | 14.18

## Loading Summary - foundation su (hidden)
|  |  | All foundations are square so B = L |  |  |  | B is in direction of x |  | L is in direction of y
[7 empty] | Foundation Depth (m) = |  |  |  | 0.75 | Foundation Depth (m) = |  |  |  | 1 | Foundation Depth (m) = |  |  |  | 2
Name | Permanent Vertical Fz (kN) | Variable Vertical Fz (kN) | ¦¦ to Span, Fy (kN) | ⊥ to Span, Fx (kN) | Moment about ¦¦, My (kNm) | Moment about ⊥, Mx (kNm) | Base Size (B)1 | e'B1 | e'L1 | Mid Third1 | Bearing1 | Base Size (B)2 | e'B2 | e'L2 | Mid Third2 | Bearing2 | Base Size (B)3 | e'B3 | e'L3 | Mid Third3 | Bearing3
400kV High Level - Post Insulator Structure x 7150mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.6 | #REF! | #REF! | #REF! | #REF! | 3.5 | #REF! | #REF! | #REF! | #REF! | 2.8 | #REF! | #REF! | #REF! | #REF!
Dead Load | 17.37 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 2.79 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0 | 8.8 | 76.5 | 0
Wind in Y direction | 0 | 0 | 5.57 | 0 | 0 | 38.22
Static Tension Load | 0 | 0 | 0 | 0 | 0 | 0
Short Circuit Load | 0 | 0 | 1.45 | 5.6 | 66.29 | 17.26
400kV Low Level - Post Insulator Structure x 2750mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.6 | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 1.3 | #REF! | #REF! | #REF! | #REF!
Dead Load | 4.69 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.63 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.44 | 2.05 | 7.91 | 2.98
Wind in Y direction | 0 | 0 | 1.85 | 0 | 0 | 6.52
Static Tension Load | 0 | 0 | 0.73 | 0 | 0 | 4.97
Short Circuit Load | 0 | 0 | 2.83 | 0 | 0 | 19.36
400kV Surge Arrester Structure x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.7 | #REF! | #REF! | #REF! | #REF! | 1.6 | #REF! | #REF! | #REF! | #REF! | 1.4 | #REF! | #REF! | #REF! | #REF!
Dead Load | 5.77 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.74 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.29 | 2.32 | 8.78 | 2.14
Wind in Y direction | 0 | 0 | 2.17 | 0 | 0 | 7.77
Static Tension Load | 0 | 0 | 0.49 | 0 | 0 | 3.59
Short Circuit Load | 0 | 0 | 3.25 | 0 | 0 | 24.06
400kV Earth Switch Structure x 2900mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4 | #REF! | #REF! | #REF! | #REF! | 2.2 | #REF! | #REF! | #REF! | #REF! | 1.8 | #REF! | #REF! | #REF! | #REF!
Dead Load | 13.47 | 0 | 0.3 | 0 | 0 | 0.27
Ice Load | 0 | 2.17 | 0.05 | 0 | 0 | 0.05
Wind in X Direction | 0 | 0 | 5.77 | 0 | 0 | 8.67
Wind in Y direction | 0 | 0 | 0 | 5.24 | 21.79 | 0
Static Tension Load | 0 | 0 | 1.57 | 0.03 | 1.95 | 2.52
Short Circuit Load | 0 | 0 | 3.82 | 2.42 | 18.68 | 5.46
400kV 3 Phase Pantograph Disconnector x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.8 | #REF! | #REF! | #REF! | #REF! | 2.5 | #REF! | #REF! | #REF! | #REF! | 2 | #REF! | #REF! | #REF! | #REF!
Dead Load | 16.54 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 1.91 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0 | 5.37 | 28.85 | 0
Wind in Y direction | 0 | 0 | 6.38 | 0 | 0 | 29.6
Static Tension Load | 0 | 0 | 1.2 | 4.65 | 32.49 | 8.41
Short Circuit Load | 0 | 0 | 0.25 | 0.25 | 4.25 | 1.75
400kV Disconnector with 2 Earth Switch Structure x 2500mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.9 | #REF! | #REF! | #REF! | #REF! | 2.2 | #REF! | #REF! | #REF! | #REF! | 1.8 | #REF! | #REF! | #REF! | #REF!
Dead Load | 15.93 | 0 | 0.3 | 0.17 | 0.15 | 0.24
Ice Load | 0 | 2.3 | 0.07 | 0.06 | 0.06 | 0.06
Wind in X Direction | 0 | 0 | 8.68 | 1.21 | 0.32 | 14.59
Wind in Y direction | 0 | 0 | 0.07 | 5.22 | 13.06 | 0.16
Static Tension Load | 0 | 0 | 1.05 | 1.04 | 5.18 | 1.1
Short Circuit Load | 0 | 0 | 3.32 | 1.44 | 3.51 | 4.72
400kV CT Structure x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.8 | #REF! | #REF! | #REF! | #REF! | 2.5 | #REF! | #REF! | #REF! | #REF! | 2 | #REF! | #REF! | #REF! | #REF!
Dead Load | 33.38 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 2.08 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0 | 6.43 | 35.96 | 0
Wind in Y direction | 0 | 0 | 4.6 | 0 | 0 | 21.45
Static Tension Load | 0 | 0 | 0 | 0 | 0 | 0
Short Circuit Load | 0 | 0 | 0 | 4.65 | 36.8 | 0
400kV CVT Structure x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.5 | #REF! | #REF! | #REF! | #REF! | 1.4 | #REF! | #REF! | #REF! | #REF! | 1.3 | #REF! | #REF! | #REF! | #REF!
Dead Load | 8.06 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.81 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.22 | 2.54 | 9.96 | 1.65
Wind in Y direction | 0 | 0 | 2.42 | 0 | 0 | 9.17
Static Tension Load | 0 | 0 | 0.36 | 0 | 0 | 2.76
Short Circuit Load | 0 | 0 | 1.77 | 0 | 0 | 13.38
132kV High Level - Post Insulator Structure x 6700mm high
132kV Low Level - Post Insulator Structure x 2400mm high
132kV High Level - Surge Arrester Structure x 6000mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.4 | #REF! | #REF! | #REF! | #REF! | 1.2 | #REF! | #REF! | #REF! | #REF! | 1.1 | #REF! | #REF! | #REF! | #REF!
Dead Load | 2.62 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.6 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.36 | 1.84 | 5.47 | 2.22
Wind in Y direction | 0 | 0 | 1.74 | 0 | 0 | 4.87
Static Tension Load | 0 | 0 | 0.61 | 0 | 0 | 3.7
Short Circuit Load | 0 | 0 | 1.07 | 0 | 0 | 6.5
132kV Low Level - Surge Arrester Structure x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2 | #REF! | #REF! | #REF! | #REF! | 1.2 | #REF! | #REF! | #REF! | #REF! | 1 | #REF! | #REF! | #REF! | #REF!
Dead Load | 1.47 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.37 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.36 | 1.17 | 2.78 | 1.67
Wind in Y direction | 0 | 0 | 1.05 | 0 | 0 | 2.29
Static Tension Load | 0 | 0 | 0.61 | 0 | 0 | 2.79
Short Circuit Load | 0 | 0 | 1.07 | 0 | 0 | 4.9
132kV Earth Switch Structure x 2600mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.6 | #REF! | #REF! | #REF! | #REF! | 1.4 | #REF! | #REF! | #REF! | #REF! | 1.2 | #REF! | #REF! | #REF! | #REF!
Dead Load | 5.26 | 0 | 0.12 | 0 | 0 | 0.11
Ice Load | 0 | 1.18 | 0.01 | 0 | 0 | 0.01
Wind in X Direction | 0 | 2.86 | 2.6 | 0 | 0 | 2.91
Wind in Y direction | 0 | 0 | 0 | 2.29 | 6.39 | 0
Static Tension Load | 0 | 2.05 | 1.23 | 0.26 | 1.21 | 1.48
Short Circuit Load | 0 | 3.39 | 1.35 | 0.91 | 4.71 | 1.58
132kV CVT Structure x 2400mm high | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.3 | #REF! | #REF! | #REF! | #REF! | 1.2 | #REF! | #REF! | #REF! | #REF! | 1.1 | #REF! | #REF! | #REF! | #REF!
Dead Load | 5.01 | 0 | 0 | 0 | 0 | 0
Ice Load | 0 | 0.49 | 0 | 0 | 0 | 0
Wind in X Direction | 0 | 0 | 0.22 | 1.81 | 5.13 | 1.17
Wind in Y direction | 0 | 0 | 1.71 | 0 | 0 | 4.59
Static Tension Load | 0 | 0 | 0.36 | 0 | 0 | 1.95
Short Circuit Load | 0 | 0 | 1.57 | 0 | 0 | 8.43
132kV CT Structure x 2400mm high
132kV Disconnector with 2 Earth Switches Structure x 2600mm high

## Graph data
| #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF!
400kV High Level - Post Insulator Structure x 7150mm high |  |  |  | #REF!
400kV Low Level - Post Insulator Structure x 2750mm high |  |  |  | #REF!
400kV Surge Arrester Structure x 2400mm high |  |  |  | #REF!
400kV Earth Switch Structure x 2900mm high |  |  |  | #REF!
400kV 3 Phase Pantograph Disconnector x 2400mm high |  |  |  | #REF!
400kV Disconnector with 2 Earth Switch Structure x 2500mm high |  |  |  | #REF!
400kV CT Structure x 2400mm high |  |  |  | #REF!
400kV CVT Structure x 2400mm high |  |  |  | #REF!
400kV Cable Sealing End |  |  |  | #REF!
400kV Circuit Breaker |  |  |  | #REF!
Super Gride Transformer |  |  |  | #REF!
132kV High Level - Post Insulator Structure x 6700mm high |  |  |  | #REF!
132kV Low Level - Post Insulator Structure x 2400mm high |  |  |  | #REF!
132kV High Level - Surge Arrester Structure x 6000mm high |  |  |  | #REF!
132kV Low Level - Surge Arrester Structure x 2400mm high |  |  |  | #REF!
132kV Disconnector with 2 Earth Switches Structure x 2600mm high |  |  |  | #REF!
132kV Earth Switch Structure x 2600mm high |  |  |  | #REF!
132kV CT Structure x 2400mm high |  |  |  | #REF!
132kV CVT Structure x 2400mm high |  |  |  | #REF!
132V Cable Sealing End |  |  |  | #REF!
132kV Circuit Breaker |  |  |  | #REF!
#REF!

## Plant Summary
|  | Number of Foundations | [5 empty] | Notes:
Notation | Structure Name | Carnaig | Banniskirk | Assigned pad size | Volume |  |  | All PI on CAD file have been assumed to be LLPI
400kV HLPI | 400kV High Level Post Insulator | 149 |  | #REF! | #REF! | Example Image |  | On CAD file DISC is displayed with one ESW above and below it. This is to show that the equipment has 2 ESW on top of it
400kV LLPI | 400kV Low Level Post Insulator |  |  | #REF! | #REF! | 132kV ESW | #VALUE!
400kV SA | 400kV Surge Arrester |  |  | #REF! | #REF!
400kV ESW | 400kV Easrth Switch |  |  | #REF! | #REF!
400kV PANTO | 400kV Pantograph Disonnector |  |  | #REF! | #REF!
400kV DISC | 400kV Disconnector with 2 ESW |  |  | #REF! | #REF!
400kV CT | 400kV Current Transformer |  |  | #REF! | #REF!
400kV CVT | 400kV Capacitative Volate Transformer |  |  | #REF! | #REF!
400kV CSE | 400kV Cable Sealing End |  |  | #REF! | #REF!
400kV CB | 400kV Circuit Breaker |  |  | #REF! | #REF!
SGT | Super Grid Transformer |  |  | #REF! | #REF!
132kV HLPI | 132kV High Level Post Insulator |  |  | #REF! | #REF!
132kV LLPI | 132kV Low Level Post Insulator |  |  | #REF! | #REF!
132kV SA HL | 132kV Surge Arrester (High Level) |  |  | #REF! | #REF!
132kV SA LL | 132kV Surge Arrester (Low Level) |  |  | #REF! | #REF!
132kV ESW | 132kV Easrth Switch |  |  | #REF! | #REF!
132kV PANTO | 132kV Pantograph Disonnector |  |  | #REF! | #REF!
132kV DISC | 132kV Disconnector with 2 ESW |  |  | #REF! | #REF!
132kV CT | 132kV Current Transformer |  |  | #REF! | #REF!
132kV CVT | 132kV Capacitative Volate Transformer |  |  | #REF! | #REF!
132kV CSE | 132kV Cable Sealing End |  |  | #REF! | #REF!
132kV CB | 132kV Circuit Breaker |  |  | #REF! | #REF!
Total volume
#REF!
nr pad sizes | 4
Pad sizes | 2.8 | m
| 2.3 | m
| 1.8 | m
1.3
#VALUE!

## Baseplates
Notation | Structure Name | Bolt depth (mm) | Bolt Spacing (mm) | Baseplate Size (mm) | Example Image
400kV HLPI | 400kV High Level Post Insulator | 300 | 450 | 550 x 550 x 30 | 132kV ESW | #VALUE!
400kV LLPI | 400kV Low Level Post Insulator | 300 | 450 | 550 x 550 x 30
400kV SA | 400kV Surge Arrester | 300 | 450 | 550 x 550 x 25
400kV ESW | 400kV Easrth Switch | 300 | 450 | 550 x 550 x 25
400kV PANTO | 400kV Pantograph Disonnector | 300 | 450 | 550 x 550 x 30
400kV DISC | 400kV Disconnector with 2 ESW | 300 | 450 | 550 x 550 x 20
400kV CT | 400kV Current Transformer | 300 | 450 | 550 x 550 x 30
400kV CVT | 400kV Capacitative Volate Transformer | 300 | 450 | 550 x 550 x 20
400kV CSE | 400kV Cable Sealing End
400kV CB | 400kV Circuit Breaker
SGT | Super Grid Transformer
132kV HLPI | 132kV High Level Post Insulator
132kV LLPI | 132kV Low Level Post Insulator
132kV SA HL | 132kV Surge Arrester (High Level) | 300 | 350 | 450 x 450 x 15
132kV SA LL | 132kV Surge Arrester (Low Level) | 300 | 350 | 450 x 450 x 15
132kV ESW | 132kV Easrth Switch | 300 | 350 | 450 x 450 x 15
132kV PANTO | 132kV Pantograph Disonnector
132kV DISC | 132kV Disconnector with 2 ESW
132kV CT | 132kV Current Transformer
132kV CVT | 132kV Capacitative Volate Transformer | 300 | 350 | 450 x 450 x 15
132kV CSE | 132kV Cable Sealing End
132kV CB | 132kV Circuit Breaker
#VALUE!

## Images
400kV HLPI | #VALUE! | #VALUE!
400kV LLPI | #VALUE! | #VALUE!
400kV SA | #VALUE! | #VALUE!
SGT | #VALUE!
400kV DISC | #VALUE! | #VALUE!
400kV PANTO | #VALUE! | #VALUE!
400kV CB | #VALUE!
400kV CT | #VALUE! | #VALUE!
400kV CVT | #VALUE! | #VALUE!
400kV CSE | #VALUE!
400kV ESW |  | #VALUE!
132kV LLPI
132kV HLPI
132kV SA HL |  | #VALUE!
132kV SA LL |  | #VALUE!
132kV DISC
132kV PANTO
132kV CB
132kV CT
132kV CVT |  | #VALUE!
132kV CSE
132kV ESW | #VALUE! | #VALUE!

## Bearing Intro (hidden)
Project No: |  | M123013 |  |  | Ref: |  |  |  | Sheet No: |  | 6 | of | 19 |  |  |  | 6
Project Name: |  | Mersey Travel Train Lengthening Phase 2 | [6 empty] | Date: |  | 2025-07-14 10:27
Calculations for: |  | Column Assessment Check | [6 empty] | By: |  | KGH
| 3.0 Foundation Check | [15 empty] | With the exception of the Sheet No, all other header information only needs to be entered on the
IntroSheet. The cells are linked to automatically repeat on all other sheets.
The following will check the prevoisly calculated design loads against the soil and foundation properties
Please note that, although the logo on these sheets appears out
of proportion, this is intentional - it compensates for an Excel
3.1 Introduction and Factors
The design has been checked in accordance with:
|  | BS EN 1997-1 : 2004 |  |  |  |  | Geotechnical Design, Part 1 General Rules
in accordance with Procedure in Annex D
|  |  | Partial Factors |  |  |  |  | SLS |  | DA1.1 |  | DA.2 |  | Favoirable
|  |  |  | Materials |  | g | j' | 1 |  | 1 |  | 1
[6 empty] | g | c' | 1 |  | 1 |  | 1
[6 empty] | g | cu | 1 |  | 1 |  | 1
|  |  |  | Actions |  | g | G | 1 |  | 1 |  | 1 |  |  | 1
[6 empty] | g | Q | 1 |  | 1 |  | 1 |  |  | 0
|  |  |  | Resistances |  | g | R | 1 |  | 1 |  | 1
As ground contains sand, a permeable matieral, no undrained calculations will be performed.
In order to demonstrate the effects of the proposed works, bearing capcaity calculations have been performed for the founadtion in it's existing and proposed coniditon,
FM-AD-002-07 | [15 empty] | Tony Gee and Partners LLP

## INPUTS (hidden)
Project No: |  | M123013 |  |  |  | Ref: | [7 empty] | Sheet No: |  |  | 7 |  | of |  | 19 |  |  | 7
Project Name: |  | Mersey Travel Train Lengthening Phase 2 | [11 empty] | Date: |  |  | 2025-07-14 10:27
Calculations for: |  | Column Assessment Check | [11 empty] | By: |  |  | KGH
3.2 Bearing Capacity Inputs (existing)
Foundation Geometry
¦¦ to Span |  | Width |  | (B) |  | = |  | 3 |  |  | m
⊥ to Span |  | Length |  | (L) |  | = |  | 3 |  |  | m
|  | Depth |  | (D) |  | = |  | 0.7 |  |  | m | BGL
Base
|  | Inclination (α) |  |  |  | = |  | 0 |  |  | deg
|  | Unit Weight |  |  |  | = |  | 25 |  |  | kN/m3 | [6 empty] | Eccentrcity (mm)
|  | Ground Properties | [5 empty] | gs
|  | Strata Name |  |  |  |  | Density |  |  | cu |  |  | j' |  |  | c' |  | thickness
[8 empty] | kN/m3 |  | kPa |  |  | Deg |  |  | kPa |  |  | m
Embedded Strata
Ground Properties from Southport desk study |  | Alluvium |  |  |  |  | 18 |  |  |  |  | 32 |  |  | 0 |  |  | 3
Founding Strata
|  | RTD |  |  |  |  | 18 |  |  |  |  | 32 |  |  | 0 |  |  | 0
|  | Ground Water Level | [6 empty] | = |  | 3 |  |  | m | BGL |  |  | SLS
|  | Worst Water Level | [6 empty] | = |  | 3 |  |  | m | BGL |  |  | DA1.1 / DA1.2
|  | Water Unit Weight | [5 empty] | (gw) | = |  | 9.81 |  |  |  | kN/m3
Characteristic Loads
Vertical Loads
[5 empty] | Dead |  |  | VGk | = |  | 17.37 |  |  |  | kN
[5 empty] | Live |  |  | VQk | = | [5 empty] | kN |  |  |  |  | B
|  | Lateral Loads | [9 empty] | HB | [7 empty] | HL |  |  |  | HB= acts in the direction of B'
[5 empty] | Dead |  |  | HGk | = |  | 8.8 |  |  |  | kN |  |  |  | 5.29 |  |  | kN |  | HL = acts in the direction of L'
[5 empty] | Live |  |  | HQk | = |  | 0 |  |  |  | kN |  |  |  | 0 |  |  | kN
|  | Moments | [9 empty] | ML | [7 empty] | MB |  |  |  | MB= acts about the B' axis
[5 empty] | Dead |  |  | MGk | = |  | 76.5 |  |  |  | kNm |  |  |  | 38.22 |  |  | kN |  | ML = acts about the L' axis
[5 empty] | Live |  |  | MQk | = |  | 0 |  |  |  | kNm |  |  |  | 0 |  |  | kN
Surcharge Loads
[5 empty] | Dead |  |  | qG0k | = |  | 0 |  |  |  | kN
[5 empty] | Live |  |  | qQ0k | = |  | 0 |  |  |  | kN
Self Weight of Foundation
[5 empty] | Dead |  |  | WGk | = |  | 157.5 |  |  |  | kN
|  |  | Weigh of any backfill | [5 empty] | = |  | 0 |  |  |  | kN
NOTE: ALL FORCES AS APPLIED TO CENTRE OF BASE (i.e B/2)
FM-AD-002-07 | [22 empty] | Tony Gee and Partners LLP
B
D
L
q
ML
HB
V

## Action Effects (hidden)
Project No: |  | M123013 |  |  | Ref: |  |  | Sheet No: | 8 | of | 19 |  |  | 8
Project Name: |  | Mersey Travel Train Lengthening Phase 2 | [5 empty] | Date: | 2025-07-14 10:27
Calculations for: |  | Column Assessment Check | [5 empty] | By: | KGH
3.3 Action Effects (existing)
[6 empty] | SLS | DA1.1 |  | DA1.2 |  |  | Units
|  | Vd total |  |  |  | 17.37 | 17.37 |  | 17.37 |  |  | kN
|  | HB total |  |  |  | 8.8 | 8.8 |  | 8.8 |  |  | kN
|  | HL total |  |  |  | 5.29 | 5.29 |  | 5.29 |  |  | kN
|  | HRES total |  |  |  | 10.2676 | 10.2676 |  | 10.2676 |  |  | kN
|  | ML total |  |  |  | 76.5 | 76.5 |  | 76.5 |  |  | kN
|  | MB total |  |  |  | 38.22 | 38.22 |  | 38.22 |  |  | kN
|  | Wd total |  |  |  | 157.5 | 157.5 |  | 157.5 |  |  | kN
|  |  | e' B |  |  | 0.43747 | 0.43747 |  | 0.43747 |  |  | m
|  |  | e' B < B/6 |  |  | MID 1/3 | MID 1/3 |  | MID 1/3
|  |  | B' = B-2e'B |  |  | 2.1251 | 2.1251 |  | 2.1251 |  |  | m
|  |  | e' L |  |  | 0.21856 | 0.21856 |  | 0.21856 |  |  | m
|  |  | e' L < L/6 |  |  | MID 1/3 | MID 1/3 |  | MID 1/3
|  |  | L' = L-2e |  |  | 2.5629 | 2.5629 |  | 2.5629 |  |  | m
|  | A' |  |  |  | 5.4463 | 5.4463 |  | 5.4463 |  |  | m
|  | u base |  |  |  | 0 | 0 |  | 0 |  |  | m
3.4 Design Bearing Pressure (existing)
|  |  | qEd | = | Σ Vd / A'
|  |  |  | = | gG (VGk+WGk) + gQ(VQk) / A'
[6 empty] | SLS | DA1.1 |  | DA1.2 |  |  | Units
|  | Vd |  |  |  | 174.87 | 174.87 |  | 174.87 |  |  | kN
|  | qEd |  |  |  | 32.1082 | 32.1082 |  | 32.1082 |  |  | kPa
|  | q'Ed |  |  |  | 32.1082 | 32.1082 |  | 32.1082 |  |  | kPa
FM-AD-002-07 | [12 empty] | Tony Gee and Partners LLP

## Summary (hidden)
Project No: |  | M123013 |  |  | Ref: |  |  | Sheet No: | #REF! | of | 19 |  |  | #REF!
Project Name: |  | Mersey Travel Train Lengthening Phase 2 | [5 empty] | Date: | 2025-07-14 10:27
Calculations for: |  | Column Assessment Check | [5 empty] | By: | KGH
3.6 Summary (existing)
|  | Resistance |  |  |  | SLS | DA1.1 |  | DA1.2 |  |  | Units
|  | Drained q'Rd |  |  |  | 150 | 150 |  | 150 |  |  | kPa
Design Bearing Pressure
|  |  | qEd | = | Σ Vd / A'
|  |  |  | = | gG (VGk+WGk) + gQ(VQk) / A' | [8 empty] | NOTE: Check in "Action Effects" tab that the load acts in the middle 1/3, row 18 and row 21
[6 empty] | SLS | DA1.1 |  | DA1.2 |  |  | Units
|  | q'Ed |  |  |  | 32.1082 | 32.1082 |  | 32.1082 |  |  | kPa
Utilisation
[6 empty] | SLS | DA1.1 |  | DA1.2
|  | q'Ed / q'Rd |  |  |  | 21.41% | 21.41% |  | 21.41%
FM-AD-002-07 | [12 empty] | Tony Gee and Partners LLP